PERFORMANCE MEASUREMENT AND MATHEMATICAL MODELLING OF INTEGRATED SOLAR WATER HEATERS

CELINE GARNIER

BEng in Energy and Environmental

A thesis submitted in partial fulfilment of the requirements of Edinburgh Napier University for the award of Doctor of Philosophy.

March 2009

# ABSTRACT

In a period of rapidly growing deployment of sustainable energy sources the exploitation of solar energy systems is imperative. Colder climates like those experienced in Scotland show a good potential in addressing the thermal energy requirement of buildings; particularly for hot water derived from solar energy. The result of many years of global research on solar water heating systems has outlined the promising approach of integrated collector storage solar water heaters (ICS-SWH) in cold climates. This calls for a need to estimate the potential of ICS-SWH for the Scottish climate.

This research project aims to study and analyse the performance of a newly developed ICS-SWH for Scottish weather conditions, optimise its performance, model its laboratory and field performance together with its environmental impacts and analyse its integration into buildings and benefits of such a heating system, for the primary purpose of proposing a feasible ICS-SWH prototype. Laboratory and field experiments were performed to investigate the performance of the newly developed ICS-SWH and the parameters affecting it which were fundamental to modelling its performance. This was followed by developing a thermal macro-model able to compare the temperature variation in different ICS-SWH designs; including internal temperature and external weather conditions for a given aspect ratio and to evaluate the performance of this ICS-SWH for laboratory and field conditions. This was followed by a three-dimensional Computational Fluid Dynamic (CFD) analysis of the ICS-SWH in order to optimise the fin spacing as a means of improving its performance. A Life Cycle Assessment (LCA) and monetary analysis considering the whole life energy of the different ICS-SWH designs were carried out using a previously developed thermal model in order to establish the most viable ICS-SWH with the smallest carbon footprint. Finally, a study to show how the ICS-SWH could be integrated into buildings and its potential benefits to builders and households was undertaken.

Through this work, important parameters for modelling laboratory and field performance of ICS-SWH are established. The innovative modelling tool developed can predict the bulk water temperature of the ICS-SWH for any orientation and location in the world with good accuracy.  Improvements of the ICS-SWH fin design were suggested through the CFD analysis while keeping the costs to a minimum. The ICS-SWH prototype showed a high commercial potential due to its environmental and monetary benefits as well as its potential for integration into commonly used solar water heating installations and modern methods of construction such as roof panels which could result in a viable commercialisation of the prototype.

# ACKNOWLEDGEMENTS

I would like to take the opportunity to thank my supervisors Mr John Currie and Prof Tariq Muneer for their support and guidance throughout the course of my research. Furthermore, I am grateful for the assistance I have received from the technician Mr Ian Campbell and his practical know-how. Further, I would like to give my appreciation to the PhD student Haroon Junaidi and my friend Alexander Scott-Tonge for providing advice and support throughout my research. My coach and friend Alexandra Stellatou was supporting me everyday of my present tenure for which I am sincerely grateful. Finally, this research would not have happened without the love and support of my friends and family.

C’est dans l’effort que l’on trouve la satisfaction et non dans la réussite. Un plein effort est une pleine victoire.

The pleasure lies in making the effort, not in its fulfilment.

Gandhi, Extrait des Lettres à l'Ashram

# DECLARATION

I hereby declare that the work presented in this thesis was solely carried out by myself at Edinburgh Napier University, except where due acknowledgement is made, and that is has not been submitted for any other degree.

……………………………………………

CELINE GARNIER (CANDIDATE)

…………………..

Date

# TABLE OF CONTENTS

ABSTRACT…….	i

ACKNOWLEDGEMENTS	ii

DECLARATION	iii

TABLE OF CONTENTS	iv

LIST OF FIGURES	ix

LIST OF TABLES	xiv

NOMEMCLATURE	xv

CHAPTER 1	INTRODUCTION	1

1.1	Energy	1

1.1.1	Energy, environment and society	1

1.1.2	Current energy scenario	2

1.2	Energy issues and challenges	7

1.2.1	Implications set by the global energy scenario	7

1.2.2	Energy policy and prospects of renewable energy	12

1.3	Prospect of SWH in UK and Scotland	15

1.3.1	Energy and Environmental Scene in Scotland	15

1.3.2	Solar market and prospects	16

1.3.3	Need for affordable SWH and data modelling (prospect of solar water heating for Scotland)	18

1.4	The Present Research Project	19

1.4.1	Problem statement	19

1.4.2	Aims and objectives	19

1.4.3	Outline of the thesis	20

1.5	Concluding remarks	21

CHAPTER 2	REVIEW OF THE RELEVANT LITERATURE	22

2.1	Solar water heaters	22

2.1.1	Solar hot water systems	22

2.1.2	Solar thermal collectors	23

2.1.3	Solar water heater parameters	31

2.2	Modelling the solar water heater	38

2.2.1	Macro model – Thermal model	38

2.2.2	Micro model – Computational Fluid Dynamics (CFD)	45

2.3	The integration of solar water heaters	47

2.3.1	Life cycle assessment (LCA)	47

2.3.2	Weather conditions in Scotland	49

2.3.3	Building integrated SWH	51

2.4	Concluding remarks	53

CHAPTER 3	LABORATORY AND FIELD EXPERIMENTS	54

3.1	Methodology	54

3.1.1	Solar water design and construction	54

3.1.2	Assessment and calibration of experiment equipment	59

3.1.3	Experimental considerations	67

3.2	Laboratory experiments	68

3.2.1	Experimental set up	68

3.2.2	Experiment results	70

3.2.3	Comparison of past and current research	73

3.2.4	Discussion of laboratory testing	81

3.3	Field experiments	82

3.3.1	Experimental test set up	82

3.3.2	Experiment results	85

3.3.3	Discussion of field testing	96

3.4	Uncertainties and errors associated with measurements	97

3.4.1	Equipment error and uncertainty	97

3.4.2	Operational errors	98

3.5	Concluding remarks	98

CHAPTER 4	MODELLING	100

4.1	Macro model – Thermal model	100

4.1.1	Purpose and Language	100

4.1.2	Capabilities and Limitations	100

4.1.3	Assumptions	101

4.1.4	Thermal network and fundamental heat transfer analysis	103

4.1.5	Modelling stratification for laboratory conditions	115

4.1.6	Digital simulation flow chart	117

4.1.7	Computational and experimental data comparison	118

4.1.8	Error analysis	135

4.1.9	Discussion of thermal models	136

4.2	Micro model – CFD	138

4.2.1	Purpose and fin optimisation	138

4.2.2	Capabilities and limitations	139

4.2.3	Model calibration	140

4.2.4	Modelling results	140

4.2.5	Discussion on CFD	147

4.3	Concluding remarks	148

CHAPTER 5	LIFE CYCLE ASSESSMENT (LCA)	151

5.1	Goal and Scope	151

5.2	Material inventory	153

5.2.1	Stainless-steel	153

5.2.2	Aluminium	153

5.2.3	Glass wool insulation	154

5.2.4	Window glass	155

5.2.5	Timber	156

5.3	Energy analysis	156

5.4	Environmental impacts	159

5.5	Interpretation	161

5.5.1	Identification of Energy and Environmental issues	161

5.5.2	ICS-SWHs energy and carbon dioxide savings	162

5.5.3	Energy payback time – EPBT	166

5.5.4	Carbon dioxide emission payback time – ECPBT	167

5.5.5	Conclusions and recommendations	169

5.6	Monetary analysis (MA)	170

5.6.1	Collector material costs	170

5.6.2	ICS-SWHs costs	173

5.6.3	Monetary payback time (MPBT) analysis	174

5.7	Comparison with other systems and limitations of the study	176

5.8	Concluding remarks	177

CHAPTER 6	INTEGRATION INTO HOUSING DESIGN	178

6.1	Towards zero-carbon homes	178

6.1.1	UK Government Initiatives	178

6.1.2	Zero-carbon housing for UK	181

6.2	Flat-plate collectors for low carbon construction	183

6.2.1	Existing flat-plate collectors	183

6.2.2	Suggested installation for the ICS-SWH	188

6.3	Integration of the ICS-SWH into roof structure	191

6.3.1	Modern Method of Construction (MMC)	192

6.3.2	SIRS Roofs	193

6.3.3	Structural issues	194

6.3.4	Integration of the ICS-SWH	196

6.4	Concluding remarks	196

CHAPTER 7	CONCLUSIONS	198

7.1	Summary of conclusions	198

7.2	Contribution to knowledge	205

7.3	Potential future work: Looking back, looking ahead	206

REFERENCES….	208

APPENDICES….	226

# LIST OF FIGURES

Fig. 1-1: Year 2006 energy share of global final energy consumption, REN21 (2008)	2

Fig. 1-2: 2006 Consumption per capita in tonnes oil equivalent, BP (2007)	7

Fig. 1-3: End of year 2006 Fossil fuel reserves to production (R/P) ratios, data from BP (2007) & WEC (2007)	8

Fig. 1-4: Year 2007 World and EU installed capacities of solar PV, solar thermal and wind power – Data from the REN21 (2007) and EC (2007)	15

Fig. 1-5: European solar market, Data from EurObserv’ER (2007) and European Commission (EC) (2007).	17

Fig. 2-1: Advertisement for the climax solar water heater in 1892, Butti and Perlin (1980)	26

Fig. 2-2: Monthly mean temperature of the storage fluid for full mixed tank and stratified tank, Cristofari et al. (2003).	32

Fig. 2-3: Hot water draw-off profiles for studies of McLennan (2006) and UK-ISES for 200l/day and 300l/day respective loads.	36

Fig. 2-4: Equivalent heat flow circuit for Cruz et al (2002) collector, insulation and losses	39

Fig. 2-5: Heat transfer mechanism in an ICS-SWH	40

Fig. 2-6: Orientation angle for air cavity regression	41

Fig. 2-7: Geometric parameter of Cruz et al. (1999) trapezoidal-shaped solar/energy store	43

Fig. 2-8: Simplified processes typically considered in LCA for a product	47

Fig. 2-9: Elements of a full LCA, Environmental-Technology-Best-Practice-Programme (2000).	48

Fig. 2-10: Yearly total global horizontal solar irradiation in kWh/m2, UK, Šúri et al. (2007)	50

Fig. 2-11: Average ambient temperature ranges in Europe for the month of January and the most probable area of winter operation for the ICSSWH design, Smyth et al. (2001).	51

Fig. 2-12: Solar collector possible integration, Jaehnig et al. (2007).	52

Fig. 3-1: Sectional view of the aluminium ICS SWH used in the present work	55

Fig. 3-2: ICS main parts after cutting, folding and drilling operations	55

Fig. 3-3: SWH main parts being assembled and welded	56

Fig. 3-4: SWH fins assembled and welded	56

Fig. 3-5: Water flow in manufactured collector – bottom right inlet pipe (bypass flow)	58

Fig. 3-6: Water flow in CAD drawings collector – bottom left inlet pipe	58

Fig. 3-7: Cold test installation	60

Fig. 3-8: Hot test installation	61

Fig. 3-9: Thermocouple positions and volume control associated, a: Aluminium collector, b: Stainless-steel Collector (Junaidi et al (2005)).	62

Fig. 3-10: Acrylic plastic tubes inserts with thermocouple slot	63

Fig. 3-11: Acrylic plastic tube inserts in pipes	63

Fig. 3-12: Assumption of thermocouple position in the SWH	64

Fig. 3-13: Energy distribution of the electrically heated silicone rubber pad	64

Fig. 3-14: Absorber sheet of the ICS-SWH	65

Fig. 3-15: Silicon paste	65

Fig. 3-16: Heating pad thermographic images: a. Silicone side (heating side), b. Front side, Scale: (C	66

Fig. 3-17: Heating pad thermographic images: Hot spots (a) and cool spots (b) represent the silicone welds. Scale: (C	66

Fig. 3-18: Test rig with control and measurement equipment	69

Fig. 3-19: Circuit diagram for control and measurement of the heat flux	69

Fig. 3-20: Temperature stratification profile for a 200W/m2 heat flux	71

Fig. 3-21: Buoyancy forces with time	72

Fig. 3-22: Temperature stratification profile after 8 hours of operation	73

Fig. 3-23: Dimensionless temperature “Th/TH” vs dimensionless distance “h/H” at 45( inclination, a: 100W/m2 heat flux input, b: 400W/m2 heat flux input	75

Fig. 3-24: Water temperature profiles of finned aluminium and stainless-steel ICS-SWHs at 400W, 45( inclination.	76

Fig. 3-25: Water temperature profiles of finned aluminium, finned and un-finned stainless-steel ICS-SWHs for eight hours of exposure time at 200W.	77

Fig. 3-26: ICS-SWH water temperature increase: un-finned versus finned stainless-steel	78

Fig. 3-27: ICS-SWH water temperature increase: un-finned stainless-steel versus finned aluminium	78

Fig. 3-28: Aluminium and stainless-steel ICS-SWH efficiency comparison at 45 degree inclination, 100W/400W	80

Fig. 3-29: Cross-sectional representation of the field tested ICS-SWH	82

Fig. 3-30: Experimental test rig	83

Fig. 3-31: Back insulation of roof simulated box	83

Fig. 3-32: Experimental test rig side insulation	84

Fig. 3-33: Field experiment data	85

Fig. 3-34: One day field experiment data	86

Fig. 3-35: Sky radiation effect on cover temperature with kc as the clear sky index	87

Fig. 3-36: Energy network for clear sky conditions	88

Fig. 3-37: Stratification with time and solar radiation	88

Fig. 3-38: Dimensionless longitudinal stratification: Th / Tbottom versus h/L	89

Fig. 3-39: Efficiency line for the ICS-SWH studied	91

Fig. 3-40: Stratification in the ICS-SWH and water temperature draw-off	93

Fig. 3-41: Draw-off profile and performance	94

Fig. 3-42: Ante Meridian dimensionless longitudinal stratification with draw-off: Th / Tbottom Vs h/H	95

Fig. 3-43: Post Meridian dimensionless longitudinal stratification with draw-off: Th / Tbottom Vs h/H	96

Fig. 4-1: Thermal network of the system	104

Fig. 4-2: Heat flux exchanges occurring at the ICS-SWH	105

Fig. 4-3: Dew-point and ambient temperatures relationship for clear days	109

Fig. 4-4: Dew-point and ambient temperatures relationship for overcast days	109

Fig. 4-5: Geometric parameters of the ICS-SWH (blue nodes denote fluid temperature measurements locations)	110

Fig. 4-6: Straight rectangular fins of uniform cross section and energy balance for an extended surface	111

Fig. 4-7: Dimensionless fin temperature versus fin length	113

Fig. 4-8: Dimensionless temperature stratification after 8 hours	115

Fig. 4-9: Simulated fin heat transfer rate	118

Fig. 4-10: Simulated fin temperature drop where  is the excess temperature achieved assuming 90% of heat is conducted through the fins.	119

Fig. 4-11: Simulated fin heat transfer coefficient	120

Fig. 4-12: Simulated fin heat transfer rate with time – Aluminium 3mm SWH	120

Fig. 4-13: Simulated fin efficiency	121

Fig. 4-14: ICS-SWH efficiency with time for 400W/m2 heat flux applied	122

Fig. 4-15: Computational and experimental comparison for 250W/m2 heat flux	123

Fig. 4-16: Computed vs Experimental water temperatures	123

Fig. 4-17: Computed vs Experimental stratification after 8 hours of operation for all heat inputs	127

Fig. 4-18: Computed vs Experimental stratification after 22 hours for all heat inputs	128

Fig. 4-19: 200W/m2 data - Computed vs Experimental stratification after 8 hours of operation	129

Fig. 4-20: Validation of the model - Computed vs Experimental stratification after 8 hours of operation	130

Fig. 4-21: Computed and experimental data for a five day period in July 2007	131

Fig. 4-22: Computed vs Experimental for a five day period in July 2007	132

Fig. 4-23: Simulated effect of wind velocity on water temperature for a five day period in July 2007 where V0, V2, V4 and V6 represents the wind velocity values of 0m/s, 2m/s, 4m/s and 6m/s respectively	133

Fig. 4-24: Computed vs Experimental for a 50 day period in July	134

Fig. 4-25: Temperature stratification of fins and middle line of water collector	141

Fig. 4-26: Velocity profile – 4 fins, top view, after 20 min	142

Fig. 4-27: Velocity profile – 4 fins, side view, after 20 min	142

Fig. 4-28: Longitudinal water temperature stratification – 4 fins, front view, after 20min	143

Fig. 4-29: Longitudinal water temperature stratification – 4 fins, side view, after 20min	144

Fig. 4-30: Velocity profile – 5 fins, top view, after 20 min	145

Fig. 4-31: Velocity profile – 5 fins, side view, after 20 min	145

Fig. 4-32: Longitudinal water temperature stratification - 5 fins, side view, after 20min	146

Fig. 4-33: Heat transfer and water temperature profiles in the ICS-SWH	147

Fig. 4-34: Total data - measured and computed for a 50 day period: 7th June – 27th July 2007	150

Fig. 5-1: Sectional view of the aluminium ICS SWH. Note: a dimension drawing is shown in Figure 3-1	152

Fig. 5-2: Glass wool production process, Source: ERIMA (2007)	155

Fig. 5-3: Window glasss production process, Source: Made How (2007)	156

Fig. 5-4: Useful energy saved annually for each ICS-SWH	164

Fig. 5-5: Solar fraction of AL-3, AL-1.5 and ST-1.5. Note: solar fraction is the amount of energy provided by the ICS-SWH divided by the energy required to raise water temperature to 55oC	165

Fig. 5-6: Annual CO2 savings by fuel type using ICS-SWHs	166

Fig. 5-7: ICS-SWH ECPBT: Categorisation with respect to fuel type	168

Fig. 5-8: Cost comparison	171

Fig. 6-1: Towards zero carbon homes: a. RuralZED, b. Ecohouse, c. Lighthouse, d. Sigma	182

Fig. 6-2: Separate solar tank pre-heating the dwelling hot water tank	184

Fig. 6-3: Combined solar dwelling hot water tank.	185

Fig. 6-4: External heat exchanger	186

Fig. 6-5: Combi-boiler solar compatible installation	187

Fig. 6-6: Solartwin system	188

Fig. 6-7: ICS-SWH installation	191

Fig. 6-8: Structural Insulated Roof System - SIRS, Wood (2006)	193

Fig. 6-9: Structural Insulated Roof System, James Johns roof trial.	194

Fig. 6-10: Installation schematic and final installation of VELUX windows, VELUX (2005)	195

# LIST OF TABLES

Table 1-1: Emission rates of energy sources (DEFRA, 2008a)	3

Table 2-1: Details of draw-off patterns used by Junaidi et al. (2008)	36

Table 2-2: Critical angle versus aspect ratio, Hollands et al. (1976)	41

Table 3-1: Aluminium and Stainless-steel physical properties at 300K	57

Table 3-2: Equipment and Specifications	59

Table 3-3: Stainless-steel vs aluminium overall efficiencies for different heat flux: Note laboratory tests	81

Table 3-4: Daily hot water demand profile	92

Table 4-1: Overall improvement factor for given parameters	122

Table 4-2: Statistical indicators values – Total Data	126

Table 4-3: Statistical indicators values – Total Data	129

Table 4-4: Statistical indicators values	132

Table 4-5: Statistical indicators values	134

Table 5-1: Embodied energy of materials	157

Table 5-2: Mass balance of the collectors	158

Table 5-3: Embodied energy and incidence of materials on the energy balance	158

Table 5-4: Energy analysis for a 3m2 installation	159

Table 5-5: Embodied carbon dioxide of materials	160

Table 5-6: Embodied energy and impacts of materials on the energy balance	160

Table 5-7: Total CO2 emissions for a 3m2 installation	161

Table 5-8: EPBT	167

Table 5-9: ECPBT	168

Table 5-10: Raw material costs per square meter of collector	173

Table 5-11: Case 1 - Collectors MPBT depending on auxiliary heating system for a 3m2 system	175

Table 5-12: Case 2 – Overall ICS-SWHs MPBT	175

# NOMEMCLATURE

Abbreviation and Symbols

EPBD		Energy Performance of Buildings Directive

EPDM		Ethylene Propylene Diene M-class rubber

ICS-SWH	Integrated Collector Storage Solar Water Heater

LZCT		Low and Zero Carbon Technologies

MBE		Mean Bias Error

MMC		Modern Methods of Construction

RMSE		Root Mean Square Error

SWH		Solar Water Heater

SIRS		Structural Insulated Roofing System

Greek and Subscripts

bulk water temperature						(K

water temperature at local point					(K

bottom collector water temperature					(K

top collector water temperature					(K

water temperature at t= i						(K

water temperature at t= i+1						(K

initial water temperature at t= 0					(K

ambient temperature							(K

absorber plate temperature						(K

glass cover temperature                                                                   	(K

sky temperature							(K

dew point temperature							(K

fin temperature at fin position x					(K

temperature difference of the water at a time interval		(K

rise in mean water temperature 			(K

excess temperature at x=0 = base of the fin ()		(K

dimensionless temperature ()

depth of the collector							m

vertical length in the collector	 ()			m

total length of the collector                                     			m

local length in the collector						m

dimensionless length ()

tilt angle of the absorber plate						rad

buoyancy force							N

density of the water at the bottom of the collector			kg/m3

density of the water at the top of the collector 			kg/m3

the standard gravity of  9.81N/kg					N/kg

the time interval in second						s

G((()e 	rate of incident solar radiation transmitted                                    	W

heat flux applied to the (solar) Collector Surface			W/m2

useful energy transferred to the water					W

water-ambient energy lost						W

absorber plate-water energy lost					W

glass cover-surrounding heat loss					W

absorber plate-glass cover energy lost				W

total energy transferred from the fins to the water			W

fin heat transfer rate  per stripes					W

absorber plate-glass cover overall U-value				W/(K

water-ambient overall U-value					W/(K

glass cover-ambient overall U-value					W/(K

absorber plate-water overall U-value  (=)				W/(K

resistance of the insulation material					(K/W

resistance occurring at the box surface in contact with the wind	(K/W

absorber plate-cover convection coefficient				W/m2. (K

glass cover-ambient external convection coefficient			W/m2. (K

absorber plate-water convection coefficient				W/m2. (K

fin heat transfer coefficient per stripes				W/m2. (K

thermal conductivity of air						W/m. (K

thermal conductivity of water						W/m. (K

thermal capacitance of the water					J/(K

specific heat of the collector material					J/(K

thermal capacitance of the insulation					J/(K

thermal capacitance of the wood box					J/(K

thermal capacitance of the glazing					J/(K

overall thermal capacitance of the material				J/(K

overall thermal capacitance of the system				J/(K

wind speed								m/s

tilt angle of the absorber plate						rad

cross sectional area							m2

fins area  						m2

thickness of the fins							m

width of the fins							m

perimeter								m

fins position								m

strip length taken equal tofor modelling			m

d	depth of the fins							m

(         Stefan-Boltzmann constant						J/s.m2.(K4

IP 	improvement factor

number of fins

emissivity of the glass cover

emissivity of the absorber plate

bulk emissivity temperature of the absorber plate

bulk emissivity temperature of the glass cover

sky emissivity

# INTRODUCTION

This chapter reviews present day energy usage, current energy issues and challenges, prospects for renewable energy and in particular potential for solar energy. It also discusses the requirements for studies on solar water heaters (SWH) and specifically introduces the potential for integrated collector storage solar water heaters (ICS-SWH) in the UK and contextualises the current research. It also summarises the problem statement and objectives of the present research and provides an outline of the thesis.

## Energy

### Energy, environment and society

Energy, by definition, is the capacity to perform work. Solar energy supports virtually all life on Earth through photosynthesis and drives the climate and weather. This energy can be developed by means of a variety of natural and synthetic processes. Plants capture solar radiation by photosynthesis and convert it to chemical form, while direct heating or electrical conversion is used by solar equipment to generate electricity or to do other useful work. Even the energy stored in widely used energy resources like petroleum and other fossil fuels was originally converted from sunlight by photosynthesis over time.

Energy use and supply plays an essential role in society and human life. Economic development and the wellbeing of society are closely linked to energy. The continual growth in populations and venture for a better economy resulted in a dramatic increase of energy consumption, particularly in the last two centuries due to the increase of available energy sources. With the evolution of society, humans progressively gained access to larger amounts of energy and increased significantly their energy consumption primarily in the more developed nations to cover industrial, transport, space-heating, lighting and refrigeration needs. Modern societies use more energy every year for industry, services, homes and transport and take for granted easily available energy.

However, the increasing concern of climate change and the effect of burning fossil fuels as well as global awareness of the limited supply of fossil fuels such as oil, coal or natural gas shows that energy does define and constrain our progress. Thus, to optimise the future of our society the allocation of Earth’s energy resources needs to be understood and prioritised.

### Current energy scenario

World energy sources can be divided into two main categories: non-renewable and renewable. Non-renewable energy sources define energies which cannot be replenished in a short time period and that eventually become too expensive and too environmentally damaging to recover. Worldwide, non-renewable energy sources are predominant including fossil fuels and uranium for nuclear power. Fossil fuels range from very volatile materials like natural gas, to liquid oil, to non-volatile materials such as coal accounting for 79% of the world’s primary energy supply as shown in Figure 1-1 from REN21 (2008) data. Renewable energy sources can be replenished naturally in a short period of time and will never run out. They include solar, wind, geothermal, biomass energy as well as hydropower and ocean energy.

Fig. 1-1: Year 2006 energy share of global final energy consumption, REN21 (2008)

Non renewable sources

Solid fossil fuels were the first energy resource used. Coal remains the world’s most abundant and fastest-growing fossil fuel in 2006 accounting for about 23% of the global power usage based on REN21 (2008) fossil fuel data and specification fuel data stated by BP (2007a) and BP (2007b). Coal remains the leading source for electricity generation as well as the largest worldwide source of carbon dioxide emissions. Oil is the leading fuel in the transport sector therefore making it very vulnerable to any disruption in oil price and supply as stated by Bucklin (2003). Oil accounted for 34.5% of the global power usage according to REN21 (2008), BP (2007a) and BP (2007b) data. Natural gas has been used for over a century for lighting and heating and is now considered a very valuable resource; being more efficient and cleaner than other fossil fuels releasing lower amounts of carbon dioxide emissions per unit energy released as shown in Table 1-1.

Table 1-1: Emission rates of energy sources (DEFRA, 2008a)

| Fuel type | Emission rates kgCO2/kWh |
| --- | --- |
| Electricity | 0.43 |
| Natural Gas | 0.19 |
| Oil | 0.25 |
| Coal | 0.30 |
| Petrol | 0.24 |
| Nuclear | 0.009 to 0.014 |
| Renewables | 0 |

World natural gas consumption accounts for 21.5% of the global power usage. BP (2007a) states that European consumption decreased mainly due to large increases in contracted prices in the UK and Eastern European countries resulting in large consumption decline. The major disadvantage in the use of natural gas is its transportation which is more complicated and expensive than other fossil fuels.

Nuclear energy accounts for 3% of the global power usage as stated by REN21 (2008). The World Energy Council (WEC) (2007) stated that at the current rate of production, using current reactor technology, global nuclear reserves are estimated to last for almost another 85 years. Its technology is sometimes promoted as a sustainable energy source that reduces carbon emissions and can increase energy security for countries with access to this technology by decreasing dependence on fossil fuel sources. However, there are political, security and environmental concerns about nuclear reactor safety as well as radioactive waste disposal and plant decommissioning.

Despite the world’s increasingly heavy dependence on this leading energy source, depleting fossil fuel resources do not make them reliable choices for the future and provide impetus for moving the economy towards sustainable energy sources.

Renewable energy

Renewable energy can be defined as energy flows which are replenished at the same rate as they are “used” as stated by Sorensen (2002). Solar radiation is the principal source of earth’s renewable energy sources. Some of the common renewable energy technologies and their current status in the global energy mix are reviewed in the following paragraphs.

Non-solar renewables

Tidal and geothermal energy do not depend on solar radiation. Tidal power traps water in a basin activating turbines generating electricity as it is released through the tidal barrage. Tidal energy power generation is still in an early stage of development and accounts for only 0.01% of the world’s energy consisting of 0.3 GW reported by REN21 (2008). However, based on a recent report from the Sustainable Development Commission (SDG) Appleyard (2007) stated that UK’s tidal resources could provide 10% of the UK’s electricity in the near future.

Geothermal energy meaning “Heat from the Earth” is the energy generated by the heat contained within the Earth. Geothermal energy is used for power and for heating. Trapping geothermal energy for power generation can be achieved using hydrothermal reservoirs, hot dry rock, geopressure brines and magma, each with engineering challenges and constraints making them not always practical or economically feasible. Low temperature geothermal resources by heat extraction from the near sub-surface of the Earth have been widely used in the past and provide energy for space, water heating, district heating, greenhouse heating or warming of fish ponds in aquaculture. The relatively constant temperature of the top 15 metres of the Earth's surface can be used to heat or cool buildings indirectly through the use of heat pumps. The report published by REN21 (2008) states by the end of 2007 worldwide use for electricity had reached 10 GW, with an additional 33 GW used directly for heating with half being geothermal heat pump installations and accounted for 0.2% of the global energy usage.

Solar energy: Indirect uses

Solar energy can be converted indirectly to useful energy by other energy forms. Solar radiation drives a hydrologic cycle by causing evaporation, precipitation and surface run-off. Hydropower is defined as the energy of moving water and has been exploited for many years for irrigation purposes or watermills. The largest hydropower in use today generates electricity by transforming potential energy of water stored at an elevation into kinetic energy by the rotation of a turbine rotating the motor to produce electricity. Based on REN21 (2008) report hydroelectricity generates about 16% of the world’s electricity in 2006 consisting of 770 GW of large hydro plants and 73 GW of small hydropower installation.

Solar radiation results in differences of temperature in the atmosphere and oceans in such manner that the convective currents produce winds, ocean currents and waves.

Wind power has been commonly used for centuries by windmills for pumping water or crushing corn. Wind power can be produced on a large scale such as on land-based or offshore wind farms connected to electrical grids or by individual wind turbines providing electricity to isolated rural areas. Wind is now one of the most advanced renewable energies due to its mass production, improvement in quality, reliability and cost effectiveness. REN21 (2008) reported that wind power capacity accounts for 74 GW or 0.3% of global energy usage.

Wave power uses ocean surface motion caused by winds and is mainly used for electricity generation. Most companies and infrastructures are concentrated along the UK coastline according to Cameron (2007). A tremendous amount of energy is available in ocean waves though initial technical problems associated with this technology have delayed its development.

Biomass, and especially the fuels derived from biomass named Biofuels, is another indirect manifestation of solar energy. Biofuels have recently been subject to increasing attention as interest in sustainable fuel sources grows. Traditional biomass accounts for about 9% of the 13% of global biomass energy usage as stated by REN21 (2008). Biomass can be classified as a renewable resource if a sustainable balance is therefore maintained between carbon emitted and absorbed. The combustion of biomass fuel emits CO2 to the atmosphere, however emission are no more than the amount it absorbed during its lifetime growth. Biomass is used in power and heating with an estimated capacity of 45 GW in 2006 in Europe with two third used for heating.

Solar energy: Direct uses

Solar energy is often seen as the fuel of the future and represents the energy generated directly from the sun. Applications vary from the residential, commercial, industrial, agricultural and transportation sectors. Solar energy can be used in two main ways to produce heat and electricity.

Solar electricity generation has been developed primarily through photovoltaic (PV) and solar thermal power generation. PV is generally used for small and medium-sized applications and can be grid-connected or autonomous. REN21 (2008) reported that PV connected grids represent the fastest growing global power generation technology reaching an estimated cumulative installed capacity of 7.8 GW at end of 2007. REN21 (2008) estimated the cumulative existing solar PV at 10.5GW by the end of 2007 accounting for about 0.03% of the global energy usage.

Concentrating solar thermal power (CSP) generation is more commonly built for large-scale electricity generation. This system uses direct solar radiation concentrated by lenses or mirrors and tracking systems to provide high temperature heat for generating electricity or directly generating electricity by using PV. Today, total installed CSP capacity is estimated by REN21 (2008) to be 0.4GW accounting for about 0.002% of global energy usage. However, the World Energy Council (2004) reported that on a long term scenario, the contribution of CSP could reach 630GW by 2040. These technologies however have limited use in cloudy locations as they require direct solar radiation.

Solar thermal applications are the most widely used solar energy technology and include solar cooking, detoxification, desalination or solar thermal systems. Solar distillation, pasteurisation and desalination purify water using solar radiation by means of different processes. Solar drying and solar ponds are different thermal methods to provide process heat to dry agricultural products, clothes or to reach high temperature for chemical reactions and melting of metals. Solar cookers capture sunlight which is converted to heat retained for cooking. Solar cookers are used for cooking, drying or even pasteurising water and milk. It can be a real solution for problems such as fuel poverty, impure milk and drinking water and health problems caused by indoor air pollution from combustion of hydrocarbon faced by developing countries often with high solar energy potential.

Finally, solar thermal collector applications are the most widely used solar energy technology for domestic hot water and space heating using only sunlight to heat water. Different designs and techniques are available depending on the application and temperature required. Glazed solar water heaters (SWH) such as flat plate collectors, batch systems or evacuated tube and air collectors typically used for space heating are the most common types while unglazed collectors are generally used for heating swimming pools. SWH systems are described in more detail in Chapter 2. SWH systems are efficient and reliable technologies compared to other solar technologies and are gaining ground in a few countries. REN21 (2008) reported that SWH existing capacities accounted for 105GWTh in 2006 or 1.3% of the global energy usage and was estimated to reach 128GWTh in 2007; accounting for a total installed collector area in use around the world of 183 million square meters.

## Energy issues and challenges

### Implications set by the global energy scenario

The global energy demand is increasing worldwide and will continue to rise as developing nations reach developed status and developed nations maintain their modernisation trends. Figure 1-2 from BP (2007a) reveals that the energy consumption per capita is significantly higher in developed states than in less developed and developing countries.

Fig. 1-2: 2006 Consumption per capita in tonnes oil equivalent, BP (2007)

IEA (2006) reports that energy demand is projected to grow on average by 1.6% a year thus an increase of just over one-half between 2006 and 2030. Over 70% of this increase would come from developing countries such as India and China which alone would account for 30%. Today’s worldwide energy use is 80% fossil fuels which is to remain the dominant source of energy until 2030 in the Reference Scenario reported by IEA (2006).

However, the current global use of fossil and nuclear fuels has many consequences including the depletion of natural resources, threat to the world energy security and global climate change caused by emissions of greenhouse gases from fossil fuel combustion. These consequences have many environmental, economical and political impacts over the world.

Non-renewable resources and their liability

Fossil fuels stocks are rapidly depleting around the globe. At current consumption rates, BP (2007) and WEC (2007) state that proven world reserves should last between 40 to 150 years depending on the fuel as shown in Figure 1-3.

Fig. 1-3: End of year 2006 Fossil fuel reserves to production (R/P) ratios, data from BP (2007) & WEC (2007)

Pressure on existing reserves is increasing daily due to increased demand. Monbiot (2004) reported that the world currently consumes six barrels of oil for every new barrel discovered. Energy experts suggest that oil production will probably peak sometime between 2004 and 2010 as stated by Asif et al. (2007), followed by natural gas. The general decline of fossil fuel production will cause a global energy gap which could result in serious international, economic and political crises and conflicts detailed further in section 1.2.1.3.

The price of oil has been rising because demand is growing faster than a finite supply. Based on data from Asif and Muneer (2007) the cost of crude oil per barrel increased by 50% between 2004 and 2005.  IEA (2006) states that rising oil and gas demand could accentuate the consuming countries vulnerability to severe supply disruption following a price shock. Nuclear energy could be a possible route to reduce the energy gap however environmental and political concerns associated with this technology do not make it a favourable approach especially with the current existence and growth of green energies.

Other concerns recently raised are the vulnerability of current energy infrastructures to adverse weather conditions. Depletion of water could result in serious problems as vast amounts of water are required for fuel processing and cooling in fossil fuel, nuclear and geothermal power plant as stated by Gleick (1994). Met Office (2003) and Jowit & Espinoza (2006) outlined the 2003 and 2006 heat wave consequences on the operations of several power plants. Plants were put at risk and were shut down due to lack of water to cool the condensers. Other components such as gas and oil pipelines or transmission line could be affected by extreme weather.

This energy scene is facing another major challenge and is raising serious environmental concerns associated with fossil fuel consumption and production.

Environmental concerns

Energy production, distribution and consumption raised serious environmental concerns over the last century. Climate change is defined by the UN (1992) as “a change in climate that is attributed either directly or indirectly to human activity that alters the composition of the global atmosphere and which is in addition to natural climate variability observed over comparable time periods.”.

Climate change is caused by an increase of greenhouse gases by natural processes or by human activities. For the last 150 years, atmospheric concentrations of greenhouse gases have been steadily increasing partly due to the industrialisation revolution of human activities. Carbon Dioxide (CO2) is one of the main greenhouse gases which is primarily produced from burning fossil fuels and deforestation. Other gases such as methane and nitrous oxide predominantly produced from agricultural activities and changes in land use or halocarbons and sulphur hexafluoride released by industrial processes contribute to climate change. Maplecroft net Ltd (2007b) reported that world carbon dioxide emissions in 2025 are projected to reach 38.8 billion tons, exceeding 1990 levels by 81%.

Climate change is already happening and its first signs can be witnessed around the globe. IPCC (2007) reported measurements recording an increase of  0.74 ± 0.18(C in mean global surface temperature from 1906 to 2005 against the baseline of 14(C from Sims (2004) and predicted a rise by 1.4 to 5.8°C during the 21st century. As a result, mean sea level rose by 10 to 20cm with an average rate increase of about 3.1 ± 0.7mm per year from 1993 to 2003. IPCC (2007) reported that since 1993 thermal expansion of the oceans has contributed to 57% of the sea level rise while melting glaciers and ice caps contributed for about 28% and polar ice sheets contributed for the remaining 15%. Asif et al. (2007) stated that sea level is projected to rise by about 50cm during the 21st century with a range of 15 to 95cm. These projections have been backed up by recent satellite data from IPCC (2007) showing an annual Artic sea ice reduction of 2.7 ± 0.6% per decade since 1978, with larger decreases in summer of 7.4 ± 2.4% per decade. Mountain glaciers and snow cover on average have declined in both hemispheres with snow cover decline of 10% since the late 1960s in the mid and high latitudes of the northern Hemisphere. Maplecroft net Ltd (2007a) showed that there was a general increase in precipitation in many regions of the world with a decline only observed over Northern Hemisphere sub-tropical regions while UNEP and UNFCCC (2001) described scenarios of worsening intensity in parts of Africa and Asia. Some extreme weather events have changed in frequency and intensity over the last 50 years such as heat waves, heavy precipitation events, intense tropical cyclone activities and incidence of extreme high sea-level making climate change one of the main challenges of today.

Economic, health and political impacts

The impacts of depleting fossil fuels and climatic changes have been a major source of dispute and are all inter-linked. Climate change impacts will lead to economic losses for various sectors around the world. According to the Stern Review (2006) if action is not taken to curb carbon emissions, climate change could cost between 5 and 20 percent of the annual global gross domestic product. These increases in costs arise from extreme weather, including floods, droughts and storms.

Health impacts as a direct result of climate change are also immense. The World Health Organisation (2008) stated that climate change led to people dying every year from its side-effects through deaths in heat waves, and in natural disasters such as floods, as well as influencing patterns of life-threatening vector-borne diseases such as malaria and an increase in food insecurity, water shortage and other multiple stresses. According to the IPCC (2007) people living in poverty would be worst affected by the effects of climate change.

Other stresses such as global economic and political instability are subject to attention. Conflicts and possible shortages of energy supply have already started to have important implications. OECD (2008) showed potential water related tensions emerging between nations that share common freshwater reserves. Access to water, its allocation and use are becoming increasingly critical concerns that may have profound consequences for political and social stability. With worldwide demand for energy increasing every day, dependency on oil imports for most developed countries and therefore energy insecurity is also becoming an increasing problem. This results in profound economic and political implications such as the 1953 coup in Iran organised by the US and Britain, followed by the Suez crisis to the Gulf War in 1991 and the Iraq war of 2003. Many wars have been conducted and are still fought all over the world to ensure corporate control over oil. Tensions are increasing on new discovery of oil. Disputes between countries over oil reserves represent another potential concern. The recent example of the Russian expedition aiming at strengthening Russia’s claim of the oil and gas wealth beneath the Arctic Ocean by planting their country’s flag on the seabed shows the potential extent of the conflict. Countries bordering the Artic including Russia, the US, Canada and Denmark, have launched competing claims to the region.

With worldwide demand for energy increasing every day, the development of new, clean, renewable energy sources is critical to Earth's environment. Worldwide and in the United Kingdom (UK), work is under way on a variety of potential answers to the global energy challenge. Energy policy and the potential of renewable energy for the environment are discussed.

### Energy policy and prospects of renewable energy

Kyoto Protocol and the energy policy of UK

Political considerations over the security of supplies, environmental concerns related to global warming and sustainability are major political issues and the subject of international debate and regulation.

As a result international treaties such as the United Nations Framework Convention on Climate Change (UNFCC) (2008) were formed at the United Nations Conference on Environment and Development.  The treaty aimed to achieve the stabilisation of greenhouse gas concentrations in the atmosphere at a level that would prevent dangerous interference with the climate system. Parties have been meeting annually in Conferences of the Parties (COP) to assess progress in dealing with climate change and to establish legally binding obligations for developed countries to reduce their greenhouse gas emissions. As a result, the Kyoto Protocol was adopted by COP-3 on December 11, 1997 and finally implemented on February 16, 2005 during the COP-11. This international agreement legally binds most industrialised countries to reduce emissions of gases contributing to climate change by an average of 5.2% below 1990 levels between the years 2008-2012, defined as the first emissions budget period. The Kyoto Protocol was the first step towards a truly global emission reduction regime. However, the commitment period of the Kyoto Protocol ends in 2012 and a new international framework needs to be negotiated and ratified to deliver the strict emission reductions. The recent COP-13 held in Bali achieved agreement on a timeline negotiation on the post-2012 framework as a successor to the Kyoto Protocol. Negotiations will be held in Poland during December 2008. To date, 178 nations have ratified the treaty, only the USA and Kazakhstan have signed but not ratified the Kyoto Protocol. Under the international Kyoto Protocol and European Union agreements the UK must reduce its baseline greenhouse gases emissions by 12.5% by 2012.

Further steps in this direction were added by the UK Government which has set its own international and domestic energy strategy to reduce carbon emissions in the Energy White paper (2007), the Climate Change Bill (2007) and more recently in the Climate Change Act 2008. The Energy White Paper: “Meeting the Energy Challenge” addresses a commitment to reduce carbon dioxide emissions, with consequent constraints to its energy policy. A mandatory 60% reduction in CO2 emissions below the 1990 baseline by 2050, with an intermediate target of between 26% and 32% by 2020, was published within the Climate Change Bill by DEFRA (2007). A review of the Climate Change Bill published by DEFRA (2008b) resulted in the recently transition to the Climate Change Act 2008 committing the UK to cut emissions by 80% by 2050. Along with this new reduction, the Energy White Paper outlines the importance to ensure secure, clean and affordable energy. The Scottish Executive (2003) agreed a more stringent overall target compared to UK with its own energy policy aspiring to meet 40% of its energy through renewables by 2020. Further steps in support of this aspiration were proposed by the Scottish Government (2007 & 2008) such as the introduction of the Renewables Obligation Scotland (ROS) providing an incentive to supply higher levels of renewable energy and encourage developers to bring forward new renewable energy schemes and the Climate Change (Scotland) Bill setting a 80% beneath 1990 baseline by 2050 target, with an intermediate target of 50% by 2030.

Role and prospects of renewable energy

Ensuring a secure, clean and affordable supply of energy is essential towards the sustainable development of a modern society. Renewable energies are potential solutions to provide energy with zero or almost zero emissions therefore reducing local and global atmospheric emissions. Solar energy is the most abundant energy resource on earth and is available for use. According to the World Energy Council (2007) the annual solar energy intercepted by the surface of the Earth is approximately 180PW, therefore, more than 75,000 times the world’s total annual primary energy consumption of 14TWh. Other major renewables were estimated at 61TW such as wind, biomass, hydro and geothermal. There are therefore plentiful sources of energy that can meet the present world energy demand with appropriate technology. An increasing share of renewable energy in the energy portfolio would offer a certain degree of manoeuvrability against sudden fossil fuel energy price increases and therefore create a secure long-term sustainable energy supply.

“Renewable sources of energy have a considerable potential for increasing security of supply in Europe. Developing their use, however, will depend on extremely substantial political and economic efforts. (…) In the medium term, renewables are the only source of energy in which the European Union has a certain amount of room for manoeuvre aimed at increasing supply in the current circumstances.  We cannot afford to neglect this form of energy.” Green paper on the security of energy supply (2001).

With the recent energy policies and protocols described in section 1.2.2.1 and based on energy policy goals of the Energy White Paper, the role and prospects for renewables appear to be good. Renewables can enhance diversity in energy supply markets and secure reliable and sustainable energy supplies. They can therefore reduce occurrence of energy poverty increasing with energy pricing and reduce atmospheric emissions. Renewables can also promote competitive new markets in the UK and beyond to meet specific needs for energy services.

According to Maplecroft Ltd (2006), while emissions of developed countries are likely to stabilise, emissions from developing countries continue to rise steadily and are expected to equal those of developed countries. These developing countries often possess large amounts of renewable energy potential especially for solar applications. The knowledge transfer of such technologies to help developing countries reduce emissions as their economies grow is vitally important to their economic development.

Renewables such as solar, wind, hydropower and biofuels are potential candidates to meet global energy requirements in a sustainable way. Figure 1-4 shows a comparison of world wide and EU installed capacities of three intermittent renewables; namely photovoltaic (PV), solar thermal and wind power. These data include China which dominates the solar thermal world market with over 60% of the global installed capacity.

Fig. 1-4: Year 2007 World and EU installed capacities of solar PV, solar thermal and wind power – Data from the REN21 (2007) and EC (2007)

The published comparison of PV, solar thermal and wind capacities looks different if European data are considered. Wind power is the leader of the three technologies and is already a market reality. Solar thermal is a strong second place with many applications for the direct use of solar thermal energy in space heating, and cooling, water heating, crop drying and solar cooking. It is most used for water heating hot water being a necessity in today’s lifestyle. In some countries, residential and commercial water heaters consume a substantial portion of the average utility bill and are dependent particularly upon the combustion of fossil fuels.

## Prospect of SWH in UK and Scotland

### Energy and Environmental Scene in Scotland

An understanding of current energy supply and demand of the UK and Scotland is vital to develop an appreciation of the opportunities of SWH. Scotland consumes 175TWh of delivered energy consuming 9.1% of UK energy with only 8.5% of the UK population showing greater energy consumption per capita than the average for the UK in total.

The main end-use sectors can be divided in four: domestic, transport, industry and services. The domestic sector is the largest consumer with an energy split of 34%. A more detailed picture of the energy used in the domestic sector show that 10.1% of the total consumption in the UK is used by Scotland, despite the fact that it represents 8.5% of the UK population.

The colder climate in Scotland is a major factor explaining this figure. Scotland typically has 10% more degree-days than the UK average consequently affecting the requirements for space heating. The main fuels used in the domestic space and water heating account for over 80% of a household's energy consumption according to the Scottish Executive (2006) are gas, along with coal and oil.

The domestic sector consumes 56TWh in total. If the 80% accounting for space and water heating were to be replaced by renewable energy, then 44.8TWh of energy would be carbon neutral which would result in a decrease in CO2 emission of 12.14GtCO2/year based on the Scottish Executive (2006) data.

There is vast scope in addressing the energy requirement, particularly for hot water from renewable sources.

### Solar market and prospects

Certain parameters play a key role in the behaviour of SWH performance, such as geographic location, solar potential, types of SWH and others which could explain why they are more developed in some areas. However, their potential are nowadays valuable in any location.

There was a solid growth of 44.3% in the European solar thermal market in 2006 corresponding to more than 3 million m2 of newly installed surface of solar thermal collectors operating in Europe. The greatest growth occurred in the French market with a growth rate of over 83.1%, while the market is still dominated by Germany with a growth of 27% despite the consecutive decrease of investment subventions granted in the framework of the German market stimulation program as stated by EurObserv’ER (2007). The European market is dominated by Germany, Greece, Austria and France with over 77% of the market represented by these countries. The EU has reached an average capacity in operation of 30.8 kWth/1,000 inhabitants. This indicator makes it possible to directly compare different countries involvement in developing solar thermal applications as shown in Figure 1-5. National values range from 511 in Cyprus and 240 in Austria to less than 1 kWth/1,000 inhabitants in some Baltic countries. The UK position in the market is towards the lower end with only 252,160 m2 of solar thermal collectors in operation in 2006 which accounts for only 1.2% of the market. This indicator shows that the margin of progression is still very large in Germany and that this potential has barely been tapped in France, Spain and the UK. Figure 1-5 also shows that despite the higher available solar radiation of Spain, France and the UK there has been lower involvements in developing solar thermal compared with other European countries with lower solar radiation availability.

Fig. 1-5: European solar market, Data from EurObserv’ER (2007) and European Commission (EC) (2007).

Cyprus is the European leader when it comes to ability to capture solar energy with over 90% of the buildings equipped with solar collectors, which is twice as much as Austria and Greece. However if the whole EU was at the same level per capita as Austria today, the annual EU market would be over 170 millions m2, with a capacity in operation of about 119 GWth. This capacity would effectively substitute large amounts of conventional fuels such as oil and gas or electricity and put Europe ahead of China in terms of the global market. In their report REN21 (2007) declared that the global market is dominated by China with annual domestic sales of well over 10 millions m2 with the EU holding only a small fraction of the world market as second.

This section shows that the UK position in the market is towards the lower end and that the UK potential for developing solar thermal applications in UK has barely been tapped.

### Need for affordable SWH and data modelling (prospect of solar water heating for Scotland)

In a period of rapidly growing deployment of sustainable energy sources the exploitation of solar energy systems is imperative. Solar water heating systems have been well developed in Scotland with a large choice of systems available to suit many applications. The higher annual heating loads faced by Scotland allows longer and greater savings using solar thermal power making this type of technology more effective in northern countries. The viability of such systems has been proven as the number of commercial manufacturers increased and the number of installers accredited by the Scottish Community and Householder Renewables Initiative - SCHRI (2008) registration lists increased from 33 in March 2007 to 67 in July 2008 or 51% more installers of SWH.

The Energy Saving Trust (2005) estimated commercial prices for an installed SWH in the range of £2000 to £3000 depending on the type of collector and the capacity of the system required, with an average lifespan of 20 years. According to the Scottish Solar Energy Group - SSEG (2008) about half of the hot water energy demand over the year could be provided with an average collection efficiency of about 40% for a 2-5m2 collector based on the fairly cloudy Scottish climate getting 1000kWh/m2. There is then a niche market for lower cost SWH with a lifespan and annual thermal efficiency equal or superior to current designs on the market.

Solar water heaters also have the benefit of reducing impacts on the environment by reducing carbon dioxide emissions by 0.4-0.75 tonnes per year depending on the fuel replaced according to the Energy Saving Trust (2005).  However, as energy efficiency and better design of collectors can reduce energy use; the energy expended during the manufacturing process, also called “embodied energy”, takes a more significant part of the real energy savings and payback time. It is therefore very important to consider the whole energy life-cycle of the SWH as it allows for a better assessment of its environmental impact.

Certain parameters play a key role in the success of SWH technologies such as their monetary and energy pay back period. However, their potential use or application are valuable at any location and in any application as buying coal, oil or gas fuelled substitutes do not offer the customer any financial reward. In order to encourage the installation of renewable devices, a 30% grant is available for solar thermal technologies by the SCHRI (2008) thereby increasing the SWH return- on-investment.

The result of many years of global research on solar water heating systems has outlined the promising approach of integrated collector storage solar water heaters (ICS-SWH) in cold climates. ICS-SWH are the simplest type of SWH on the market and a popular choice when choosing a design as they possess several advantages. These systems incorporate the solar collector and thermal storage tank in a single unit. Their simplicity of construction and installation make them affordable with low costs. Other advantages such as their aesthetic value, low maintenance, ease of integration in roof structures and good overall performance in overcast sky conditions make them suitable for northern hemisphere applications where this research is taken. This calls for a need to estimate the potential of ICS-SWH for the Scottish climate.

## The Present Research Project

### Project aim

Integrated collector storage solar water heaters: To study and analyse the performance of a newly developed ICS-SWH for Scottish weather conditions, optimise its performance, model its laboratory and field performance with its environmental impacts and analyse its integration into buildings and benefits of such a heating system, for the primary purpose of proposing a feasible ICS-SWH prototype.

### Objectives

The objectives of the project can thus be summarised as follows:

- To study the possible improvement of ICS-SWH under Scottish climatic conditions through the literature review; considering the large potential market for solar thermal systems.

- Following the analysis undertaken in (1), to test in laboratory conditions the newly developed ICS-SWH in order to accurately compare its performance with a previous study carried out for ICS-SWH.

- To carry field tests of the same ICS-SWH to evaluate its performance under real Scottish weather conditions.

- To develop a thermal macro-model able to compare the temperature variation in different ICS-SWH materials; including internal temperature and external weather conditions for a given aspect ratio and to evaluate the performance of this ICS-SWH for laboratory and field conditions.

- To model the ICS-SWH using Fluent 6.2 CFD (Computational Fluid Dynamics) software to estimate an optimum fin spacing to make further improvements on the current ICS-SWH.

- To determine the monetary and energy payback considering the whole life energy of the ICS-SWH using the thermal model previously developed to determine its feasibility.

- To show the integration of ICS-SWH into buildings and its potential benefits for builders and households.

### Outline of the thesis

Chapter 1 gives the introduction to the thesis, starting from a very broad subject of energy it narrows down to renewable energy then to solar energy and then further to solar water heater and more particularly to ICS-SWH. It also provides the background, statement and objectives of the present research problem.

Chapter 2 deals with the literature review covering the following topics: (a) solar hot water systems, thermal collectors and solar water heater parameters, (b) modelling the solar water heater through a macro-model (thermal model) and micro-model (CFD), (c) life cycle assessment (LCA), weather conditions in Scotland and building integrated SWH.

Chapter 3 deals with laboratory and field experiments. The methodology used is introduced followed by the test regime, measurement and data collection. It also gives laboratory experimental set-up and results with a comparison with previous work. Experimental set-up for the field tests and results of experiments are also provided. Finally an account of uncertainties and propagation of errors through both experimental set-ups is given.

Chapter 4 presents the modelling procedure of the ICS-SWH. The thermal model results and experimental data are inter-compared for laboratory and field tests by means of various statistical indicators while the micro model is used to determine optimum fin spacing.

Chapter 5 performs a LCA of different types of ICS-SWH for use in Scottish conditions including the experimentally tested system using the previously developed macro model. Using modelled bulk water temperature in the collector, performance, monetary, energy and carbon savings comparison of three different ICS-SWHs was provided by changing their material and thickness.

Chapter 6 demonstrates the potential for ICS-SWH to be integrated into buildings and the different considerations to be taken into account when choosing such SWH. Benefits in installing such heaters and possible installations scheme into buildings are also provided.

Chapter 7 draws up important conclusions from each aspect of the presented work and also discusses the potential for future work.

## Concluding remarks

This chapter provides a detailed introduction to energy, its various resources, associated issues and challenges and its current and future status. Significance of renewable energy resources was established and various such forms discussed. Solar energy was addressed in detail as this forms the basis of the present project. SWH and underlying market prospects for UK and Scotland were briefly discussed. The need for new SWH technologies was also emphasised. This was followed by stating the research problem, its aims and objectives and finally the structure of the thesis.

# REVIEW OF THE RELEVANT LITERATURE

In the context of the present research project, investigating solar water heaters has three core aspects. The first is studying the prospects and diversity of solar water heaters. It also includes a guidance to improve the configuration of solar water heaters and experimental procedures. The second aspect deals with the modelling methodology itself. The third involves solar water heating in Scotland, commercial designs and weather considerations.

This chapter is accordingly sub-divided into three sections. Section 2.1 reviews the different type of solar water heaters, their construction and the different influencing characteristics. Section 2.2 provides a comprehensive yet summarised coverage of different methods of modelling solar water heaters. Section 2.3 reviews the integration of solar water heaters into buildings under Scottish weather considerations.

## Solar water heaters

### Solar hot water systems

SWH systems are generally very simple using only sunlight to heat water. A working fluid is brought into contact with a dark surface exposed to sunlight which causes the temperature of the fluid to rise. This fluid may be the water being heated directly, also called a direct system, or it may be a heat transfer fluid such as a glycol/water mixture that is passed through some form of heat exchanger called an indirect system. These systems are used for domestic hot water or space heating. They can be classified into three main categories: (a) Active systems which use pumps to circulate water or a heat transfer fluid, (b) Passive systems (or Thermosyphon systems) which circulate water or a heat transfer fluid by natural convection and (c) batch systems using a tank directly heated by sunlight.

Active systems are also called forced circulation systems and can be direct or indirect. A system is called direct when the pump is used to circulate drinking water between the hot water storage tank and the collector. In an indirect system the pump is used to circulate a heat transfer fluid, either water or an antifreeze mixture, between the collector and a heat exchanger. Heat is transferred by the heat transfer fluid from the collector to the drinking water through the heat exchanger in the storage tank. The use of a heat exchanger reduces significantly the system efficiencies.

Passive systems simply circulate water or a heat transfer fluid by natural convection between a collector and an elevated storage tank (above the collector). The principle is simple, as the fluid heats up its density decreases. The fluid becomes lighter and rises to the top of the collector where it is drawn to the storage tank. The fluid which has cooled down at the foot of the storage tank then flows back to the collector. This system can be operated as a direct or indirect system, whereby a heat exchanger can allow the use of antifreeze to prevent frost damage during colder winter months. Since no pumps or controls are necessary, system installation costs are reduced.

Finally, batch systems have combined collection and storage functions. They are the simplest type of SWH with flow of water throughout the system being set off whenever there is water demand. Hot water is drawn to the top of the collector and replaced by cold water at the bottom. ICS systems can supply preheated water directly to the end use appliance or more commonly to a conventional water heater tank. Depending on the system, there is no requirement for pumps or moving parts. However, the system is prone to freezing, therefore draining water in the collector and pipe is advised during cold periods. These systems could also be integrated in to active or passive systems depending on the design of the house.

Active and passive SWH systems remain more common than batch SWH systems. To date, a small amount of work has given adequate consideration to the integration of batch systems, especially within domestic buildings. Batch SWH are normally used for low temperature applications such as domestic or light industry due to the low capital outlay. This makes it possible to achieve realistic capital cost paybacks during the lifetime of the systems. The three common types of built-in-storage solar collectors are described in section 2.1.3.1 below.

### Solar thermal collectors

There are three common designs of solar water heaters. In order of decreasing cost they are: concentrating collectors, evacuated tube collector and flat-plate collectors. The choice of collector is determined by the heating requirements and the environmental conditions in which it is employed.

Concentrating collectors are mostly used in high temperature solar applications such as steam production for the generation of electricity. They track the sun during the daytime and use reflectors to concentrate the sun’s energy onto the absorber. These systems however are most appropriate for applications where direct solar radiation is high. They are best suited to climates that have a high percentage of clear sky days and are therefore not so common in Scotland

Evacuated tube collector systems are principally used for domestic water heating purposes as suggested by Morrison et al. (2004). The solar absorbing surface is placed in the centre of a vacuum tube which minimises convection losses thereby increasing efficiency. However, improved efficiency is reflected in their price. They are most suited to extremely cold ambient temperatures or in situations of consistently low-light. They are also used in industrial applications, where high water temperatures or steam need to be generated where they become more cost effective.

Finally, flat-plate collectors are used extensively for domestic hot water heating applications due to performance advantages in relation to cost. They collect both direct and diffuse radiation. Their simplicity in construction reduces initial cost and maintenance of the system. Although flat plate collectors are outperformed by evacuated tubes collectors they are generally a more cost effective solution in most climates and for the majority of domestic hot water services. There are variants of flat plate collectors such as serpentine tubes, parallel tubes or integrated collector storage solar water heaters (ICS-SWH). The simplicity in construction and low cost of ICS-SWH make them an attractive and popular choice when choosing a SWH. A more detailed picture of these systems is of interest and is presented in the following section.

#### Brief history of ICS-SWH

ICS are one of the oldest solar water heater designs still in use. The first record of ICS-SWH systems was in the United States of America (USA) in the late 1800s where sufficient hot water for showering by the late afternoon on clear days was achieved.  ICS-SWH was the first patented and commercially manufactured SWH in 1891 under the trade name ‘Climax Solar Water Heater’ designed by Kemp (1891). The first detailed study on ICS tank systems was carried out in 1936 by Brooks (1936) at the University of California Agricultural Experimental Station, USA. Although ICS-SWH were a growing market, the discovery of natural gas and oil postponed investigations of ICS-SWH until 1970. After the oil crisis of October 1973, a renewed worldwide interest in solar energy was revitalised including a renewed interest in ICS-SWH. The first developments in solar energy were undertaken by passive solar enthusiastic individuals, joined later by universities and research institutions. Today solar heating and ICS-SWH is a very popular area of research worldwide encouraged by global initiatives to promote renewable energy technologies to limit greenhouse gas emissions.

A long review of technical developments of ICS-SWH to benchmark the performance of all heaters using common performance indices was carried out by Smyth et al. (2006). World-wide popular ICS-SWH were reviewed as well as the regional, environmental and economical factors that have influenced solar heaters designs. Based on this study, a review of the key components of ICS-SWH are presented in the following section

#### Key component of ICS-SWH

There are many ICS-SWH designs but generally all consist of: (a) a storage tank, (b) a heat transport fluid flowing through the collector to remove heat from the absorber, (c) a flat plate absorber which intercepts and absorbs the solar energy, (d) a heat insulating backing with baffle and insulation, (e) a transparent cover(s) that allows solar energy to pass through but reduces heat loss from the absorber.

Storage tank

Size and shape of the storage tank have a significant effect on the performance of the SWH.  Several designs of ICS-SWH have been studied over the years. The first manufactured commercially ‘Climax Solar Water Heater’ designed by Kemp (1891) was composed of four small black painted cylindrical storage tanks interconnected and mounted in a glazed wooden box insulated with felt paper. Figure 2-1 shows the advertisement of this SWH in 1892 with a purchase price of $25.

Fig. 2-1: Advertisement for the climax solar water heater in 1892, Butti and Perlin (1980)

In 1907, Haskell (1907) patented a shallow rectangular tank design increasing the surface area allowing a faster warm-up in the morning and hotter water on cloudy days. Tanishita (1970) indicates that in 1947 Yamamoto designed the first Japanese commercial SWH made of a stainless-steel piping. The same authors states that later in 1950s the closed membrane, known as plastic bag ICS-SWH, was successfully developed and commercialised in Japan.  It consisted of a large rectangular polyvinylchloride bag, with a black membrane as a bottom surface and a transparent membrane on top. Another type of storage tank was tested by Chinnappa and Gnanalingam (1973) using square coil pipes.

Garg (1975) conducted the first year long performance study of a rectangular design ICS-SWH followed by Muneer and Hawas (1984) and Muneer (1985) who proposed a simple rectangular design ICS-SWH. Muneer and Hawas (1984) compared ICS-SWH and thermosyphon collector showing that the simple and low cost ICS-SWH narrowly outperformed the thermosyphon collector. In his later study, Muneer (1985) studied the effect of the collector depth on performances. Results showed that an increase of 2cm in depth enhanced the storage volume which made the system operate at lower temperatures and so the losses are limited resulting in an increase of efficiency of 8%.

Several studies carried by Ecevit et al. (1989), Prakash et al. (1992) and Kaushik et al. (1994) suggested that a triangular storage tank can perform better due to increased natural convection. Sokolov and Vaxman (1983) showed an efficiency of 53% for their triangular ICS-SWH using a baffle plate to separate the absorbing plate from the storage volume. Ecevit et al. (1989) studied the effect of different volumes in triangular collectors showing good overall performance in all designs. A side by side comparative experimental study of a rectangular and triangular shaped ICS-SWH was carried out in 1994 by Soponronnarit et al. (1994) under identical conditions. The thermal efficiencies of the triangular and rectangular were found to be 63% and 59% respectively. Mohamad (1997) introduced a simple thermal diode to prevent reverse circulation at night time in his triangular ICS-SWH. The storage tank efficiencies improved by 15.3% using the diode. In the same year, an innovative pyramid shape was developed for Egyptian weather conditions by Abdel-Rehim (1997) providing temperature range of 40-60 (C.  In his subsequent studies Muneer et al. (2006a) launched a new SWH design with the introduction of fins. The report details side-by-side testing of a system using a novel rectangular finned ICS against a plain rectangular non-finned ICS system installed at the Din Textile Mills, Bhai Pheru, Lahore, Pakistan. Hot water demand for this study was 80°C for the dyeing process. Their research concluded that on clear days the non-finned design achieved maximum temperatures in the region of 70°C at best, whilst the finned heater regularly achieved water temperatures higher than 70°C, sometimes reaching temperature in the region of 80°C. The solar fraction of the finned heater was found to be 73% compared to 63% for the non-finned system. Using the same design, Grassie et al. (2006) performed laboratory experiments in order to optimise the collector design under Scottish weather conditions.

A recent study developed by Cruz et al. (2002) introduced a trapezoidal storage tank design for Mediterranean climates inducing a thermal stratification in the water store. The research indicated that 30% to 70% of the daily load could be covered by the ICS-SWH.

Heat transport fluid

The collector fluid in an ICS system is potable water. Water is the cheapest, most readily available and thermally efficient fluid but does freeze and can cause corrosion. A drain-back system can empty the collector to a back-up hot water cylinder at times of low temperatures and negative heat gains. Using softened water will help extend operational lifespan.

Absorber plate

The absorber plate material is a main parameter in an ICS-SWH as it has the principal function to absorb solar radiation and transfer heat to the storage fluid. As mentioned by Smyth et al. (2006), wood was one of the first materials used, later systems using plastic were developed and then replaced by new resistant material such as copper, aluminium, stainless steel and polymers with painted absorber surfaces. The use of polymer absorber has been studies by Van Niekerk et al. (1996) for parallel tubes collectors in South Africa. Polymers, compared to metals have a lower thermal conductivity and may have high temperature limitations, but they are relatively inexpensive and can offer good freeze protection. Transfer of absorbed solar energy to the storage fluid depends on the collector materials thermal conductivity. Materials such as steel, aluminium or copper are more frequently used with copper and aluminium as the most effective. Another parameter has to be looked at when choosing the collector material. It must be of satisfactory strength and durability, lend itself to manufacturing constraints and be of an appropriate cost. Capral-Aluminium-Ltd (2006) stated that in most surroundings, aluminium has a very high resistance to corrosion. Aluminium is covered by a thin effective coating of impermeable oxide which protects from further oxidation. However, this material should be used by itself as in most combinations with other metals galvanic corrosion occurs. Several studies carried out by Stickney and Nagy (1980), Burton and Zweig (1981), Bainbridge (1981) and Tiller and Wochatz (1982) and recently Tripanagnostopoulos and Yianoulis (1992) suggested the use of an optional selective coating for absorber plate. Coatings can be applied such as electroplated black nickel, black chrome, and copper oxide or anodized aluminium. All studies showed that coatings enhanced the heat transfer and protected the absorber plate. To maximize efficiency, their absorptivity should be at least 0.9 and emissivity less than 0.1.

Insulation

Back heat losses

Early systems were simply exposed tanks of water left out to warm in the sun. These systems suffered substantially from ambient heat losses, particularly at night-time and during non-collection periods. Wide theoretical and experimental studies on an ICS SWH undertook by Garg and Rani (1982) in India proposed a baffle plate to reduce night time losses. Collector performance improvement was found during night time in addition to during the day. They also observed that by using an insulation cover during cooling hours, the collector performance could be improved by 70%. Kaushik et al. (1995) carried out a comprehensive evaluation of a triangular ICS system with a baffle. They concluded that the thickness and the material of the baffle had little impact on the system performance and that the inclusion of the baffle had a significant benefit on the system performance during non collection periods. Smyth et al. (2003) and Tripanagnostopoulos and Souliotis (2004) proved that collector performance improvement is closely linked with collector box efficacy. The baffle should be weather-proof, guard the absorber, insulate from the environment, reduce convection and conduction losses and provide a sturdy housing to hold the components. The collector box should also be designed to allow for roof integration. Gaskets and seals are further important parameters in maintaining a weather-tight seal between components whilst allowing thermal expansion of the components. Without them, moisture would fog the glazing thereby reduce transmittance and possibly damage the insulation and the absorber coating.

Muneer et al. (2006a) and Grassie et al. (2006) explained that the insulation of the storage tank was essential to protect from conduction and convection heat losses. Both authors proposed an easy solution using 0.05m of glass wool insulation on all sides of the collector housed in a wooden box. Insulation is usually between 25mm and 150 mm and ideally would have reflective foil to reflect thermal radiation back to the absorber. Common insulation materials are high-temperature resistant fibreglass batting, semi-rigid board or mineral wool. Insulation should have a low thermal expansion coefficient and should not melt or outgas at collector stagnation temperatures.

Top heat losses

Another way to decrease heat losses is the addition of a lid on top of the SWH. Moveable insulated lid were introduced by Baer (1975) resulting in a significant improvement in the heat retaining properties of the ICS-SWH. Early attempts by McCracken (1978) using materials such as Transparent Insulating Material (TIM) in order to minimise heat losses caused decreases in the system efficiency. However, recent studies of Reddy and Kaushika (1999) and Henderson et al. (2006) showed that the use of new TIM has led to greater collection performances.

Transparent cover

Bishop (1983), Duffie and Beckman (1991) and Smyth et al. (2006) established that the use of one or more transparent covers reduced thermal losses by radiation and convection by restricting air movement. Furthermore, covers protect the absorber and selective coating (if applicable) from harm, dirt, rain and other environmental factors. Glass or plastic sheets are the most common materials used for covers. The same authors indicated that the most important property required of the transparent cover material is high transmittance of solar radiation, as any loss in transmittance will lead to a direct reduction in collection efficiency. Glass is considered more appropriate than plastic as it is more durable and does not degrade in sunlight or at high collector temperatures. The only disadvantages of glass material are the more expensive costs and the possibility of impact damage. Duffie and Beckman (1991) suggested the use of additional covers to reduce convective losses. However, increase in glazing would result in higher transmission losses. Bainbridge (1981) showed that using selective coating glazing could result in enhancing greenhouse effect and maintain high transmission. Glazing with very high solar transmittance, such as AR coatings used in PV application by Gombert et al. (1998), could result in cost effective alternative for solar thermal application.

Studies conducted by Muneer et al. (2006a), Henderson et al. (2006) and Grassie et al. (2006) using a 4mm thick glass sheet to cover the top of the box collector and maintaining an air gap of 35mm established good collector performance.

#### Advantages of ICS-SWH

Rectangular ICS-SWH have several advantages over other systems. The direct contact of the working fluid with the absorber plate increases the system efficiency by eliminating the need of a heat exchanger used in most heating systems. The absence of conduits and connecting pipes to the storage tank results in eliminating the bulk heat losses appearing in other type of systems. Other advantages of ICS-SWH are the effective use of direct and diffuse radiation as well as the absence of solar tracking requirements and minimal maintenance as well as their low cost and good overall performance. They can be designed such that they seamlessly integrate in roof structures giving them an additional aesthetical and architectural value.

### Solar water heater parameters

#### Optimum angle of inclination

Different studies show different optimum angle of inclinations for Edinburgh city. Duffie and Beckman (1974) stated an optimal angle to be 0.9 times the latitude of the location. This asserts the collector tilt can take values from 0° at the equator to 90°, in Polar regions and would be 50° in Edinburgh. Reiss and Bainbridge (1978) in their research showed that systems in higher northern latitudes are often optimised for winter collection and are therefore tilted 5 to 10( more than the angle of latitude. Another research carried out by Muneer et al. (2006b) based on 27 year irradiance data for Edinburgh established that higher irradiation occurred at 30° inclination for a south facing wall. However, irradiation is not the only factor influencing a solar water heater. A more recent study conducted by Henderson et al. (2007) showed that an ICS-SWH would perform better in Edinburgh at 50° compared to 35° because of its higher Nusselt number value. The study covered the behaviour of the water cavity collector for different inclination angles. The effects were evaluated using two modes of analysis in conjunction; Computational Fluid Dynamic (CFD) software and experimental testing. The authors found another advantage of having an angle of 50° compared to 35° would be the reduction of heat losses for higher inclination angles. For regions with lower latitudes, increasing the tilt angle initially improves the thermal efficiency. However, any successive increase in tilt would reduce the efficiency as the solar gain value would become very low. Based on these past studies, an inclination angle of 45( south was implemented.

#### Stratification

Thermal stratification is an important parameter in the efficient operation of solar collector systems.  Several authors [Van Koppen et al. (1979), Furbo and Mikkelsen (1987) and Van Berkel (1996)] highlighted the importance of stratification in detached vertical storage tanks of solar water heating systems. The merits of stratification were then described by Hollands and Lightstone (1989) who demonstrated that SWH systems operating with thermally stratified storage tanks have substantially improved performance, particularly at low flow rates. Comparisons between stratified and mixed tanks were carried out by Van Berkel (1996) and Cristofari et al. (2003). Van Berkel (1996) demonstrated that mixed water tanks performed disappointingly in terms of output and collection efficiency compared to a well stratified tank. Cristofari et al. (2003) studied the performance of a classical solar water heating installation with a flat plate thermal collector and water tank storage for storage in low flow conditions installed at a Mediterranean site, Ajaccio, Corsica, France. Results showed that a stratified tank has higher performance than a fully mixed tank with monthly mean temperatures varying from 19.3(C to 69.7(C for a fully mixed tank and from 20.1(C to 71.2(C for a high thermal stratified tank illustrated in Figure 2-2.

Fig. 2-2: Monthly mean temperature of the storage fluid for full mixed tank and stratified tank, Cristofari et al. (2003).

Thermal stratification in ICS-SWH has been observed in much research but poorly analysed. Only four studies on stratification in ICS-SWH were reported by Muneer (1985), Burns et al. (1985), Smyth et al. (1999) and Henderson et al. (2006). The Muneer (1985) study involved change of vessel depth and showed no significant influence of performance with change of depth. Burns et al. (1985) evaluated an insulated single glazed rectangular wooden box containing a 250l black painted drum at a tilt angle of 40( in San Diego, California, USA. His research concluded that thermal stratification was very important in the efficient operation of ICS-SWH systems, however, it was suggested that these systems should only be used for preheating. This research is limited, however as tests were only carried out for eight days in April and thus cannot predict the hot water production for a year period. Smyth et al. (1999) developed a heat retaining ICS-vessel. His research showed that reduced vessel wall conduction and thus convective motion and fluid mixing, improved thermal stratification. Finally, the last research in date of thermal stratification in ICS-SWH was performed by Henderson et al. (2006) who developed one of the first studies on thermal stratification for a rectangular ICS-SWH at various inclinations and constant heat flux values. The authors showed that stratification played an essential role in defining the heat gain characteristics when the storage tank was in direct contact with the heating surface. Experiments and CFD analysis were performed and showed that the degree of stratification in the ICS-SWH depends upon the angle of inclination, the exposure time and the incident insolation. The same author posited that stratification in solar water heaters can be roughly divided into two classes: (a) static mode, (b) dynamic mode. The static mode is a limited study of temperature for fully or partially charged heaters, while a dynamic mode deals with charging and discharging cycle.

Several methods are suggested in the literature to maintain and promote stratification in storage tanks by utilizing sleeves partitions, baffles, porous intake manifolds and low flow rates. A water storage tank would naturally remain stratified until water is supplied to the load. As the hot water leaves the tank and fresh cold water is infused, mixing occurs and as a result of flow circulation leads to de-stratification.   The location of the outlet and inlet pipes should then be designed in accordance to the stratification studies to not destroy stratification into the water tank. Gertzos and Caouris (2008) investigated the influence of ten different inlet and outlet port placement on the velocity field. His research concluded that the most suitable arrangement consisted in the inlet and outlet ports placed sideways and in opposite position in order to not destroy stratification in the ICS-SWH.

Modelling stratification has been subject to much research. Several multi-node stratified tank models have been developed and compiled by Duffie and Beckman (1991).  Most recent research on stratification was carried using the transient simulation package TRNSYS to simulate thermal stratification in water storage tanks such as Cruickshank and Harrison (2006) and Jordan and Furbo (2005). However, existing models are only applicable to vertical storage tanks as a separate component of the collector. To the knowledge of the author, no stratification model has been presently suggested for inclined ICS-SWH.

The literature showed thermal benefit of high stratification and emphasised the use of low flow rates as being essential for the good performance of a collector, however improved mixing in the tank results in higher rates of heat transmission. Then stratification is important but good mixing in some case would result in better performances for the SWH. Stratification is significant when trying to optimise the collector for draw off as it helps to provide temperatures closer to those required for domestic hot water systems. Stratification is critical to evaluating the actual heat content inside the heater, which is vital for estimating the efficiency. Therefore, further research is required in modelling stratification for ICS-SWH.

#### Draw-off characteristics

The word “Draw-off” refers to the collection of hot water from the collector. The study of draw off patterns from an ICS-SWH is important in order to evaluate the practical performance and thus the effective output of the collector. Draw-off characteristics can be organised in four sections. First, hot water temperature to be achieved and hot water consumption, representing the total water drawn-off, need to be identified for the UK. Then the flow rate of water draw-off varies and is of primary importance. Finally, the time of the day the water is drawn-off, thus the draw off pattern, needs to be identified.

The hot water consumption within a domestic property is dependent upon the property size, the number of occupants, household income, lifestyle habits and the type and number of end-use appliances. The primary domestic uses of hot water includes bathing/showering, hand washing, clothes washing and dish washing. Muneer (2001) indicates that the approximate temperature requirements for domestic hot water are 40°C for baths/showers and hand basins, 50°C for dishwashing by hand and up to 80°C for clothes and dish washing machines. Courtney (1977) reports typical delivered hot water temperature in the region of 50°C to 60°C which are then diluted with cold water or electrically heated at the end-use appliance to achieve the desired temperature. Reliable data on domestic hot water consumption is diverse and some of the available information is dated. Whittle (1978) indicates demand for hot water consumption can be anywhere between 36 l/day/person to 56 l/day/person at a delivery temperature of 55°C.  However, in a 1998 Energy Follow Up Survey conducted on behalf of DTI (2005) and DEFRA an average 39 litres per day for washing machines, baths and showers with a further 10 litres for assumptions about the use of hot water at sinks and basins was suggested per person per day. According to EUROPA (2006) an average European uses 36 litres of 60°C hot water per day. A recent survey conducted by McLennan (2006) examined the water consumption through a typical day for Scottish households. The survey was carried out for 32 properties monitoring hourly activity for domestic hot water appliances over a one-week period. The average number of people living in a household was 2.44 persons, comparable to the UK-Census (2001) average of 2.36 persons per household in 2001. The hot water consumption took account of all instantaneous heaters such as electric power showers, water heated internally by domestic appliances i.e. washing machines and dishwashers, and hot water drawn from boilers or hot water tanks that is not used for space heating. The average weekday hot water consumption for all properties surveyed was 49.9 l/day/person based on a delivery temperature of 55°C.

As stated before, hot water requirement varies between households. The flow rate and pattern of water drawn are important parameters to the performance of the heater. Hollands and Lightstone (1989) suggested that low flow rates from the storage tank can improve the system performance. Fanney and Klein (1987) also investigated the influence of the collector and heat exchanger flow rates on the performance of the SWH. Lowering the collector fluid flow rate for direct systems resulted in improvements to the thermal performance of the heater. This was attributed to better stratification within the solar tank and a significant reduction in mixing, which occurred between the solar and auxiliary heated portions in the single tank. Until the 1980s flow rates were commonly around 0.015 kg/m2.s as stated by Duffie and Beckman (1991). Lower rates are recently being used such as 0.002 to 0.006 kg/m2.s in Sweden where flow rates are given per m2 of collector area.

It is important to review the different draw-off patterns, utilised in the past in order to determine the optimum draw off profile for the present research. When water is drawn off the corresponding quantity of cold water enters the ICS at the bottom, thereby decreasing the temperature, which takes time for the store temperature to recover. Several studies have been carried out on draw-off profiles in the UK. An investigation by Courtney (1977) showed that if the period of peak water demand occurred in the evening rather than the morning, annual heat output would increase by approximately 0.5 GJ for a 4 m2 solar collector delivering 170 l/day. Evening peak demands ensure solar contributions are utilised and there are no significant overnight losses that may occur with a poorly insulated hot water heating system, however lower tank temperatures achieved through daytime draw-offs can allow collectors to operate more effectively. Cruz et al. (2002) utilised the British Standard domestic heating load profile as the model for the simulation of water demand in his trapezoidal ICS-SWH. Different draw-off profiles can be found for the UK. Typical demand profile data from UK-ISES supplying 300l/day are represented in Figure 2-3 compared to a more recent study carried out by McLennan (2006) for 32 Edinburgh households. His study showed hot water draw-off profile for a 4 m2 ICS system supplying 200 l/day for a property occupied by four persons, assuming 50 litres per day per person. In both hot water draw-off profiles, significant periods of hot water demand are between 8am and 9am and 7pm to 8pm.

Fig. 2-3: Hot water draw-off profiles for studies of McLennan (2006) and UK-ISES for 200l/day and 300l/day respective loads.

Another more recent study for Edinburgh was carried out by Junaidi et al. (2008) for an ICS-SWH connected to a water tank. Four draw off patterns were studied shown in table 2-1 below.

Table 2-1: Details of draw-off patterns used by Junaidi et al. (2008)

| Draw-off pattern | 1st Draw-off Volume / time | 2nd Draw-off Volume / time | 3rd Draw-off Volume / time | 4th Draw-off Volume / time |
| --- | --- | --- | --- | --- |
| A | 25l | 09:00 | 25l | 10:00 | 25l | 13:00 | 25l | 17:00 |
| B | 25l | 08:00 | 25l | 09:00 | 25l | 12:00 | 25l | 17:00 |
| C | 50l | 10:00 | 50l | 19:00 |  |
| D | 50l | 12:00 | 50l | 19:00 |  |

The research suggested that solution A and B could achieve a temperature of 40(C in the tanks. Scheme B was suggested as the best in terms of total energy extraction. Junaidi et al. (2008) show the benefit in having four draw offs instead of  two and therefore classified the four draw-off scheme from best to worst: B, A, D, C. However this draw-off profiles negate the advantage of the integrated tank within an ICS-SWH. Therefore, more realistic draw-off scheme such as McLennan (2006) are generally preferred.

#### Performance characterisation of an ICS-SWH

The various types of ICS-SWH developed over time have impelled the need for a common criterion to measure the effectiveness of SWH. As a result, organisations such as the European Solar Collector and Systems Testing Group, ESCSTG (1989), developed a standard testing procedure for all forms of SWH used in the European Community (EC). In the USA, the ASHRAE Standard-95 (1981) also developed standards procedures in order to assess short term testing performance of SWH. The widely used test procedure proposed by the ESCSTG based on a combination of test methods showed a realistic ICS-SWH performance representation allowing a direct comparison with other experimentally investigated ICS-SWH. As stated by Smyth et al. (2006), the collection efficiency is similar to the Hottel-Whillier-Bliss equation developed by  Hottel and Whillier (1955) and Bliss (1959) for distributed type solar collectors, but applies to diurnal system performance. Collection efficiency is plotted against values of where is the average insolation on the collector aperture and  is the difference between the water temperature of the heating period and ambient temperature over the same period. This performance method is applied to flat plate collector working in steady state mode. It can be applied to ICS-SWH; however it is not representative of the actual system performance as it is not a steady state situation.

Direct comparison of measured system performances is relatively straight forward; however, predicting the performance of an ICS-SWH at another location or with a different installation configuration is more challenging. Therefore a review of the different methods to predict ICS-SWH performances was carried out in the following section.

## Modelling the solar water heater

### Macro model – Thermal model

As stated above, predicting the performance of an ICS-SWH is a challenging task. A model able to predict water temperature in an ICS-SWH would be a useful tool to allow any user to predict the performance of the installed SWH, depending on the orientation and location. Builders could use such a tool to demonstrate the performance of the ICS-SWH and the benefit of such installation.

The first study to propose and use computer simulation to predict ICS-SWH performance was conducted by Garg et al. (1972) using a single node system. Burns et al. (1985) developed an analytical model to predict the performance of a stratified ICS-SWH. Good agreement between theoretical and experimental results was reported. Later studies by Cruz et al. (2002) investigated the energy saving potential provided by a trapezoidal-shaped solar collector. This was evaluated experimentally and by computation, using a thermal network analysis model based on Luiz (1985). The thermal network showing the equivalent heat flow circuit collector, insulation and losses is showed in Figure 2-4. A full scale experimental test rig was employed to validate their modelling. Despite good agreement of simulation and experimental results, the authors failed to account for two factors. First, the heat capacity of the system was neglected. Second, tests were carried out in a laboratory which is unrepresentative of field conditions. Thus, there is a need to develop a more accurate device to predict performance for ICS-SWH. Junaidi (2007) developed a similar program for fluid flow and heat transfer generating bulk water temperatures for a rectangular shaped ICS-SWH using specific parameter such as a constant heat flux for the day. The experimental and computed temperatures were found with a deviation of 10%. These models are limited as they can not be applied to real weather conditions. There is therefore a need to develop an improved model able to predict the bulk water temperature inside the collector for any weather condition and account for different ICS-SWH design parameters. To achieve such a program, heat transfer mechanisms in the collector need to be reviewed and assessed.

Fig. 2-4: Equivalent heat flow circuit for Cruz et al (2002) collector, insulation and losses

The three heat transfer mechanisms, conduction, radiation and convection, occur inside the SWH and result in heat losses or gains. An ICS-SWH is an assembly of two natural convection cavities composed of an air cavity, represented by the space between the absorber plate and the glass cover, sitting on top of a water cavity. Convective behaviour of both cavities are different for a given angle of inclination as they operate at different Rayleigh numbers and most likely have dissimilar geometrical dimensions as their aspect ratio. Both cavities are insulated by a batch system where conduction is occurring. A representation of an ICS-SWH heat transfer mechanism is represented in Figure 2-5.

Fig. 2-5: Heat transfer mechanism in an ICS-SWH

The different mechanisms emerging from the system are detailed below:

- Convection from two parallel inclined plates at different temperatures (air cavity)

- Convection from an inclined flat plate (water cavity)

- Convection from cover to the environment

- Convection from box to the environment

- Radiation from plate to cover

- Radiation from cover to sky

- Conduction through box

- Heat capacitance of the system

A review of widely used equations for natural convection and radiation are detailed below.

#### Natural convection from two parallel inclined plates – air cavity

Natural convection in air cavities has been studied by many researchers and is a well-established phenomenon. Hollands et al. (1976) presented new experimental measurements on free convective heat transfer rates through inclined air layers of high aspect ratio, heated from below. The Rayleigh number ranged from subcritical to 105; the range of the angle of inclination “” was between 0 and 70 degrees. Although it was anticipated that the results might be identical to the results for the horizontal layer if one replaced “Ra” by “”, significant departures from the introduction of the angle were observed. As a result of their study, Hollands et al. (1976) recommended a relationship giving the Nusselt number as a function of expressed below. This expression has been since widely accepted.

(2.1)

The notation * implies that, if the quantity in brackets is negative, it must be set equal to zero. Restriction in usage of this relation are that H/L ≥ 12 and 0˚< ≤, where, is the critical tilt angle which varies with the aspect ratios as represented in Table 2-2.

Table 2-2: Critical angle versus aspect ratio, Hollands et al. (1976)

| H/L | 1 | 3 | 6 | 12 | (12 |
| --- | --- | --- | --- | --- | --- |
|  | 25( | 53( | 60( | 67( | 70( |

The Rayleigh number is expressed below:

(2.2)

Equation (1) has been found to give excellent results when applied inside the regime described above. The angle depends on the orientation of the hot surface as shown in Figure 2-6.

Fig. 2-6: Orientation angle for air cavity regression

#### Natural convection from inclined flat plates – water cavity

Many studies have been carried out on inclined heated plates [Fuji and Imura (1972), Churchill and Chu (1975), Fussey and Warneford (1978), Cruz et al. (2002)] providing a good breadth of conditions with appropriate regressions. Fuji and Imura (1972) studied natural heat transfer convection from a plate with arbitrary inclination. The heat was transferred from one side surface of two plates. The authors focused on natural convection from an isolated, vertical plate, and examined the influence of the tilt angle  over the range of and . For downward facing heating plate the authors suggested the following regression:

(2.3)

The value of the exponent  suggest a laminar flow up to values of the parameter  of . Later studies from Cruz et al. (1999) investigated buoyancy-driven convective heat exchange in a trapezoidal-shaped solar water heater. Using results from Fuji and Imura (1972), Cruz et al. (1999) developed a new formula of the Nusselt number for inclined water cavities with an estimated uncertainty of 7% expressed below:

(2.4)

Where D is the (front-to-back) bottom depth of cavity floor, H’ is the inclined height of the heater; characteristic length and U is the (front-to-back) top depth of cavity floor with Rayleigh number of equation:

(2.5)

This expression was found in good agreement with the correlation of Fuji and Imura (1972), when , indicating that the geometric parameters (D/U and H’/U) have only a small influence in comparison with the modified Rayleigh number, . The parameter H’ represents the inclined height of the heater, characteristic length. The geometric parameters of Cruz et al. (1999) are shown in Figure 2-7.

Fig. 2-7: Geometric parameter of Cruz et al. (1999) trapezoidal-shaped solar/energy store

#### Radiation from plate to cover

Duffie and Beckman (1974) suggested a standard equation for heat exchange radiation between two parallel plates such as the absorber plate and the glass cover of a collector.

(2.6)

where  is the bulk emissivity of equation ,  and are the temperature and emissivity of the absorber plate,  and  are the temperature and emissivity of the glass cover temperature, ( is the Stefan-Boltzmann constant.

#### Radiation from cover to sky

Radiation losses from the cover to the environment represent an important fraction of the total heat losses; therefore they need to be determined precisely. In a laboratory environment, only ambient conditions apply. However, in real weather conditions the system reacts differently to the environment. Radiation losses from cover to sky can be determined such as:

(2.7)

where  is the bulk emissivity of equation,  and are the temperature and emissivity of the sky.

The sky’s temperature is assumed to be equal to the ambient temperature for laboratory conditions. However, for field tests the sky acts as a black body during a clear night sky. The sky emissivity is therefore an important parameter for inclusion in models in order to simulate real weather conditions. Many correlations have been reported in literature for calculating the coefficient of emissivity inside the atmospheric transparency window such as Idso (1981), Berdahl and Martin (1984) or Cucumo et al. (2006). Equations for sky emissivity are generally valid only for clear sky conditions; as in equation (8) below developed by Cucumo et al. (2006) for sky emissivity in the atmospheric transparency window,.

(2.8)

With  		(2.9)

Where  is the atmospheric emissivity in the transparency window for clear sky conditions and  is the global emissivity.

The value of sky emissivity obtained from equation (8) is valid for clear sky conditions only. To-date only a few studies have been carried out to examine the sky emissivity under overcast sky conditions. Under an occluded or cloudy sky the emissivity, ,can be calculated from Santamouris and Asimakopoulos (1996) general relationship expressed as:

(2.10)

Where n is the total opaque cloud index, 0 for clear sky and 1 for overcast sky.

The sky temperature is also an important parameter regarding radiation losses from the cover. Many studies have been carried out on sky temperatures by Duffie and Beckman (1991), Swinbank (1963) or Berdahl and Martin (1984). Swinbank (1963) suggested a sky temperature regression of:

(2.11)

The more recent study by Berdahl and Martin (1984) used extensive data from the United States to relate the sky temperature,, to the dew point temperature, , ambient temperature and hour from midnight, t. The equation developed is expressed as:

(2.12)

The emission within the atmospheric window, and thus the sky temperature, depends on the local weather, and varies throughout the day as well as from one location to another. The sky temperature shall therefore be related to weather and time parameters to enhance the accuracy of the results; which resulted in using the Berdahl and Martin (1984) model.

By using the defined equations of the heat transfer mechanism occurring in the system, a thermal network analysis of ICS-SWH can be performed. Another approach to model ICS-SWH is the use of 3-D simulation programs.

### Micro model – Computational Fluid Dynamics (CFD)

CFD in simple terms is the use of computer and numerical methods to solve and analyse problems involving fluid flow. CFD has grown from a mathematical curiosity to an essential tool in almost every branch of fluid dynamics, from aerospace propulsion to weather prediction. Although CFD plays an important role in providing complementary information about environmental performances, it is usually unable to give an accurate prediction due to errors involved in numerical calculations. Therefore, relying solely on CFD is not recommended and results should be validated through experiments. Although CFD did not eliminate the need of experiments, it has significantly reduced the amount needed. CFD is very often used in product concept, product development and also virtual prototypes such as SWH. Fluent software is of interest for this study. It is a general purpose CFD code based on the finite volume method that offers a wide array of physical 2 and 3- dimensional (3-D) models. This software is widely used in several academic institutes and commercial research and development as it saves time and effort while maintaining a high degree of accuracy.

Recent studies indicate an increase in the use of CFD for analysing and optimising solar collector’s design and performance. The pioneering study of Gill (1966) on cavities used a finite element method to solve the flow in a square cavity. In 1983 the knowledge of flows was extended by numerical investigation of 3-D aspects by Ozoe and Fuji (1983). A finite difference technique was employed to calculate the longitudinal roll pattern and changes with angles for a cavity heated from the bottom. Based on his work, Zhong et al. (1985) inspected the influence of varied fluid properties and radiation. A comprehensive review on inclined cavities was reported by Yang (2003) whose study was based on laminar natural convective flow in inclined rectangular glazing cavities. The work on flow pattern inside the storage tank of ICS-SWH is still largely unexplored. Only two studies from the author’s knowledge have been recorded. Groenhout et al. (2002) conducted a 2-D CFD analysis involving both radiation and convection in a solar collector to compare with experimental results. CFD model results underestimated experimental data. Intensive 3-D CFD analysis on ICS-SWH was carried out by Henderson et al. (2007). His research looked at air and water cavities and at the ICS-SWH as an entity under different type of boundary conditions. The specification of boundary conditions is essential before starting any simulation. This specification consists of two elements: (a) the boundary conditions type, and (b) the location where it is applied. Boundary conditions applied to the system vary with the purpose of the simulation. Henderson et al. (2007) studied the flow behaviour of air and water cavities for different angles and different boundary conditions in order to optimise the design of the ICS-SWH. In order to compare with the results of Henderson et al. (2007) the same model boundary conditions and similar designs were used.

Once the optimal virtual design is achieved, a prototype is manufactured for testing and the technology is subjected to other assessment such as economic, energetic and environmental which can be evaluated by using life cycle assessment.

## The integration of solar water heaters

### Life cycle assessment (LCA)

Today’s economy is made of strict environmental controls and changing markets in which society is becoming progressively more aware of environmental matters. Field et al. (1993) outlined that LCA is one of the most useful tools for the study and analysis of strategies to meet the challenges of tomorrow. LCA is a method used for assessing the environmental impact by identifying the material, energy and waste flows of a product, process or activity over its entire life-cycle. The LCA of a product includes each stage from raw material extraction, manufacturing, retailing, use and maintenance to disposal or recycling. Simplified processes typically considered in LCA for a product as shown in Figure 2-8.

Fig. 2-8: Simplified processes typically considered in LCA for a product

This tool can help companies to identify necessary changes to their operations and products and as a result improve environmental performance and reduce cost. LCA methodology is a recent concept which has developed as a consequence of an enhanced awareness of environmental pressures by industry, the public and governments. LCA was initially developed by the Society of Environmental Toxicology and Chemistry (SETAC) and was later optimised by the International Organization for Standardization (ISO-14040 (2006)). LCA became progressively a more important tool for engineers, scientists, designers, managers and environmentalists.

A full LCA study includes four different phases: Goal and Scope Definitions, Life Cycle Inventory Analysis, Life Cycle Impact Assessment and finally the Interpretation. Numerous studies have been carried out on LCA identifying the four phases of LCA for different products [Weir and Muneer (1998), Ardente et al (2005a and 2005b), Tsilingiridis et al (2004), Crawford at al (2004), Taborianski and Prado (2004), Tan and Khoo (2005) or Asif et al. (2006)]. The relationship of these phases is illustrated in Figure 2-9. The goal and scope phase is the point at which decisions need to be made concerning the purpose of the LCA and what it is going to cover including the identification of the study's limits or system boundaries. Once the first phase is set, the inventory analysis phase provides data on environmental burdens associated with the product or system. Energy and raw material used, solid, gaseous and liquid wastes generated are examined and measured. The impact assessment estimates how the product or system affects the environment. It typically classifies the environmental burdens with the same environmental impact and then estimates their contribution to that particular environmental impact. At this stage, the main factor contributing to an environmental impact may be identified, allowing improvements to be processed. Finally, the interpretation phase can be described as an iterative process. Although issues might be identified at any stage, this phase looks objectively to the whole life cycle in order to assess improvement procedures to reduce environmental burdens associated with the product or system.

Fig. 2-9: Elements of a full LCA, Environmental-Technology-Best-Practice-Programme (2000).

A full LCA for a product, particularly for a complicated product can be a time-consuming and costly exercise; therefore the principle of streamlined LCA is often used to simplify the study. This type of study identifies the product or process characteristics that are critical in the context of the study and includes only these in the streamlined LCA. Many studies have used streamlined LCA as it offers the potential to deliver results more quickly and at a lower cost. These have been mainly conducted by Asif et al. (2005) and Asif et al. (2007b), and more particularly on ICS-SWH by Ardente et al (2005a and 2005b), Asif and Muneer (2006) and Asif et al. (2007a). In both the latter studies, the author’s research only included an account of the embodied energy and environmental impacts associated with the materials involved in the construction of the ICS-SWH. Environmental impacts were only expressed in terms of carbon dioxide emission values of the involved materials. Carrying out a LCA on a new product is of primary importance to achieve a better product. However, another parameter introduced by Asif et al. (2005) is the cost effectiveness of products and services. This parameter has become very important in today’s market; therefore, a monetary analysis (MA) can be carried out to estimate the overall costs of a project over its life. Costs such as capital, running, energy and others such as unpredicted maintenance and repair costs are normally included.

An LCA and MA were adopted to evaluate the energy usage, environmental impact and economic monetary performance of an ICS-SWH. Both assessments differ depending on the country in which they operate according to varying energy prices and local weather conditions.

### Weather conditions in Scotland

Scotland's climate and topography provide a great diversity for potential renewable energy resources, whose use could reduce fossil fuel dependence. It is surrounded by coast apart from in the south where it shares a land border with England. The Gulf Stream significantly affects the climate. Scotland is warmed by this stream and as such is much warmer than it would otherwise be. Because the sea surrounds Scotland, there is a great opportunity to generate energy with wind farms or offshore wave power as shown by Bruce (1994). Scotland has an abundant on- and offshore wind resource but its potential is limited by the environmental impact of large numbers of wind farms. Windy conditions increase heat losses from the top cover of SWH. Therefore, ways to limit heat losses have to be considered.

Solar energy in the UK and Scotland is far greater than is commonly perceived as illustrated in Figure 2-10 showing the vast potential market for solar systems.

Fig. 2-10: Yearly total global horizontal solar irradiation in kWh/m2, UK, Šúri et al. (2007)

MacGregor and Balmbro (1984) showed that Scotland has one of the best climates in Europe for solar water heating in buildings due to the regular heating profile of Scotland with a heating season lasting between nine and ten months. MacGregor and Balmbro (1984) believe Scotland's first solar priority should be for providing heat, not electricity. Scotland is a cold country where people use much more heat than electrical energy; therefore solar heating is much more cost-effective than solar electricity generation. This brings us to the main conclusion that there is much scope for renewable energy in Scotland. Tests were located in Edinburgh city (56N, 3.2W). The city is located 35m above sea level in an oceanic climate with large differences between summer and winter radiation levels. Past studies by Muneer et al. (2006b) show a peak value of solar radiance for Edinburgh of around 900W/m2 on a bright sunny summer day. However in winter conditions the majority of time the values for solar radiance are around 400W/m2.

Ambient temperatures of Edinburgh can reach freezing point and below. However, most ICS-SWHs have large thermal masses and simple compact structures which give good general resistance to freezing climates. Figure 2-11 based on the study of Smyth et al. (2001) on performance and freeze resistance capabilities of the ICS-SWH in winter conditions shows that the UK is within the range of operation for ICS-SWH.

Fig. 2-11: Average ambient temperature ranges in Europe for the month of January and the most probable area of winter operation for the ICSSWH design, Smyth et al. (2001).

Nevertheless, ICS-SWH should take this parameter into account when design and integration into building phases occurs using careful construction, good thermal insulation, fair thermal mass, properly controlled ventilation and good integration as described by Imbabi and Musset (1996).

### Building integrated SWH

Architectural quality of integration of solar thermal technologies is a major issue which is a critical factor to their success. Solar thermal systems are now becoming increasingly used in architectural design of roofs facades or balconies as shown by Jaehnig et al. (2007). SWH are typically integrated into roof designs as they can be simply and quickly installed into the cladding of the roof keeping costs relatively low. Individual collectors are now made in a wide range of size and shapes so they can fit the exact shape of the roof as shown in Figure 2-12 a and c. Facade integrated solar collectors are less usual but are increasingly appearing as an architectural design as well as generating energy. A more unusual set up is their recent integration in balconies such as in Val Thorens, France and Liepzig, Germany whose facade was renovated with added insulation and nine pre-fabricated balcony blocks on which the solar collector were mounted. The French and German buildings were renovated in 2004 and 2001 respectively with the latter shown in Figure 2-12 d. Figure 2-12 shows the different possible solar collector’s integrations.

| a- Berlin, Germany | b- Dornbirn, Austria |
| --- | --- |
| c- Mathoy/Tisun, Austria | d- Leipzig, Germany |

Fig. 2-12: Solar collector possible integration, Jaehnig et al. (2007).

Munari Probst and Roecker (2007) conducted a survey on the different perception of architects and engineers on the integration quality of building integrated solar thermal technologies. The study addressed glazed and unglazed collector solar thermal collectors, with black and coloured absorbers with different methods of integration. Four were roof integrated while six were on façades comprising a variety of building types, materials and colours. This study showed how essential teamwork is between architects and engineers in order to achieve both energy efficiency and architectural integration and how the system characteristics affecting the building appearance have an impact on integration quality. Hestnes (1999) suggested that collectors should be developed to respond to technical constraints, but should furthermore become an architectural element, conceived to be integrated into the buildings skin, to ease designer’s integration efforts and to reduce the overall costs.

Modern Method of Construction (MMC) could help to achieve this purpose. English-Partnership (2007) describes MMC as making use of more effective materials, speeding up housing delivery, enabling high standards of design quality and possibly helping to reduce resource consumption in the UK. MMC are increasingly regarded as a means of improving quality, reducing time spent on site, improving on-site safety and overcoming skills shortages in the construction of housing. MMC and advanced technologies are coming together to deliver higher performing, more sustainable and smarter buildings in order to achieve sustainable low energy houses, as Offsite 2007 showed in their last event of June 2007. There are therefore prospects for ICS-SWH integration with MMC.

## Concluding remarks

A review of the three core aspects of the research was presented herein. First prospects and diversity of solar water heater systems and collectors and more precisely of ICS-SWH was given. Solar water heater considerations such as angles of inclination, stratification, draw off characteristics and performances of SWH were also discussed. The second aspect gave an account of different methods of modelling SWH. Heat transfer mechanisms in SWH for thermal modelling presently of interest to this research project were discussed. CFD modelling as a tool for optimisation of SWH designs was also addressed. The third reviewed the importance towards further stage integration of SWH and the steps of a Life Cycle Assessment. A review of geographical and weather conditions in Scotland was provided. Finally, a brief review of building integrated SWH and MMC was also provided.

To sum up, all three steps explore above are deeply inter-related because each of them are crucial for the complete development of this research on ICS-SWH systems.

# LABORATORY AND FIELD EXPERIMENTS

Experimental research is an essential element in validating the performance of any proposed advancements of solar heating design technology particularly where significant improvements have been identified the ICS-SWH prototype. This chapter has been divided into four parts. The first part deals with the methodology adopted for the experiments by introducing the preliminary design of the solar collector followed by the test regime, measurement and data collection adopted for laboratory and field experiments. The second section examines laboratory experimental set-up and results and makes a comparison with previous work of Grassie et al (2006). Section three describes the experimental set-up for the field experiments and provides experiments results. Finally, the fourth section evaluates uncertainties and propagation of errors through both experiment set-ups.

## Methodology

An appropriate methodology must be applied to generate confidence in experimental design and results. This work builds on earlier research by Grassie et al (2006) which was based on a stainless-steel ICS-SWH design and focussed around the use of CFD modelling techniques.  Lessons were learned from the methodology employed in their test regimes and these have been significantly improved to enhance the research rigour. The knowledge so acquired also resulted in the use of a different material, aluminium, for the collector manufacture and optimisation of extended surfaces within the collector design in order to enhance the collector performance.

### Solar water design and construction

#### Preliminary Design

The design of the studied aluminium ICS-SWH is based on previous studies of Muneer et al (2006a), Henderson et al (2006) and finally the laboratory study of Grassie et al (2006) on a stainless-steel constructed ICS-SWH design.

Solar water heater design

The flat-plate type collector was designed, from 3mm thick aluminium sheets, of internal dimensions 1000x1000x50mm. Water inlet and outlet pipes, each of 22mm internal diameter, were provided on the top and bottom right side of the box. Three pipes were provided to insert thermocouples in the ICS-SWH in order to determine the internal temperature profile. To protect from convection heat losses the water tank was insulated with a 100mm thick layer of fibreglass wool on the bottom and all sides and placed inside a hard wooden box. A gap of 35mm between the absorber plate and the 4mm thick glazing reduces heat loss by restricting air movement and gave an aspect ratio of 28.57. Four fins were designed using aluminium sheets of 800x50x3mm; length, height and thickness respectively. Fins are a good means of improving performance in an inexpensive ICS-SWH and to achieve an increase in thermal and construction efficiency of the system. These fins were designed to be fixed inside the water tank joining the top and bottom surfaces and parallel to its sides, leaving a distance of l00 mm from both the top and bottom ends. Basic design and composition of the SWH are presented in Figure 3-1.

Fig. 3-1: Sectional view of the aluminium ICS SWH used in the present work

The top surface of the collector was covered with an electrically heated silicone rubber pad used to control power input during laboratory tests. It was also painted black to improve the solar radiation collection for the field experiments.

Figures 3-2, 3-3 and 3-4 show pre-assembly, welding and post-welding, respectively of the collector during manufacture.

Fig. 3-2: ICS main parts after cutting, folding and drilling operations

Fig. 3-3: SWH main parts being assembled and welded

Fig. 3-4: SWH fins assembled and welded

Collector material

The thermal conductivity of the collector material is an intrinsic parameter for effective ICS-SWH designs. The material must allow the absorption of solar radiation and heat transfer into the storage fluid. Aluminium is very effective, since its thermal conductivity of 237 W/m.(K is higher than other materials traditionally used for ICS-SWHs and was therefore chosen for the construction of the collector. Physical properties of aluminium are given in Table 3.1 referring to Incropera and DeWitt (2001) data.

Table 3-1: Aluminium and Stainless-steel physical properties at 300K

| Properties | Aluminium | Stainless-steel | Units |
| --- | --- | --- | --- |
|  | Values | Values |  |
| Density | 2702 | 7900 | kg/m3 |
| Specific heat | 903 | 477 | J/kg.K |
| Thermal conductivity | 237 | 14.9 | W/m.K |

An additional key property of aluminium is its low density which is only one-third that of stainless-steel, thus making aluminium collectors lighter and safer to install on roof structures. This material is also easily formed, machined and cast, significantly decreasing the final product price. Another main advantage is its high resistance to most forms of corrosion. Aluminium produces a natural thin surface layer of aluminium oxide which provides a highly effective barrier to the corrosion caused by air, temperature, moisture and chemical attack. Finally, almost every aluminium product can be recycled at the end of its useful life, without loss of metal quality or properties as identified by the International Aluminium Institute (2008).

#### Collector manufacture - differences with preliminary design

Discrepancies in the as built collector compared to the design drawings were observed. Critical internal dimensions were not achieved. Initial critical internal dimensions were fixed at 50x1000x1000mm providing an internal storage volume of 50 litres. The manufactured collector achieved dimensions of 991x989x47mm giving a 7.9% difference in volume corresponding to a four litres loss. Other divergences in the positioning of the inlet pipe were found. Laboratory tests where however not affected by this change in inlet pipe position due to non-flow tests; however, this modification can have major influence on a full flow field tests. A visualisation of the problem is shown in Figures 3-5 and 3-6.

Fig. 3-5: Water flow in manufactured collector – bottom right inlet pipe (bypass flow)

Fig. 3-6: Water flow in CAD drawings collector – bottom left inlet pipe

The construction errors have been addressed with the manufacturer in order to discuss ways and methods to improve design criteria for future test units. The main problems encountered in manufacture were due to the material being prone to distortion during the welding process using TIG (Tungsten Inert Gas). The use of a MIG (Metal Inert Gas) welding process to reduce the heat input and reduce distortion will be considered for the construction of future units. According to the manufacturer the dimensions attained were realistic for a one-off prototype.

Inlet and outlet pipes of 22mm internal diameter were chosen as the nearest commercially available products which can be tapped to suit a standard valve. Pipe diameters were changed to another standard 13mm diameter by the manufacturer. This is important when considering the integration of ICS-SWH into buildings.

### Assessment and calibration of experiment equipment

A rigorous calibration of experimental devices assures that the system will produce accurate and repeatable results with a specified degree of confidence.

#### Thermocouples

K-type thermocouples using nickel-chromium and nickel-aluminium alloys to generate voltage were used in the experiments as they fulfilled the application temperature range and were the most accessible type.

Thermocouple Calibration

The calibration process consisted of a two point cold and hot test. The equipment used for the calibration and their respective specifications are summarised in Table 3.2 below.

Table 3-2: Equipment and Specifications

| Number | Equipment | Specification | Origin |
| --- | --- | --- | --- |
| 2 | Data logger type 1F8 | Grant Instrument Squirrel 2020 series Type 1F8 Resolution up to 6 significant digits Resolution: 0.1(C | Grant Instrument |
| 1 | Thermos Flask | Insulated flask for cold test. Filled with water | Napier University |
| 1 | Constant temperature bath | MV2401, 300W, 200/250V, 500ml Maximum temperature: 150°C Liquid: Water | Electrothermal |
| 2 | Witness Thermometers | Accurate thermometers calibrated by British Standard. Two range used: 0-10°C and 50-90°C | Calibration: British Standard |
| 27 | Thermocouples | Single, K type, Accuracy: (0.5(C Temperature range: -200 to 1350(C | Napier University |
| 1 | Software | SquirrelView Plus, 2020 logger set-up, download and data export application for Windows and export data direct to Excel. | Grant Instrument |
| 1 | Computer |  |  |

Cold test:

All thermocouples were placed in a thermos flask filled with ice. Their temperature readings were recorded by the data logger after stabilisation of the temperature. A reference British Standard thermometer of range 0-10C was placed in the ice to act as a witness measure. Figure 3-7 shows the installation.

Fig. 3-7: Cold test installation

Hot test:

A constant temperature bath was used to provide uniform water temperature distribution. The bath was filled with water within which the thermocouples were placed. Thermocouple temperature readings were recorded by the data logger. Reference British Standard thermometers of range 50-90  C and 70-100  C were positioned in the hot bath to calibrate the thermocouples. Figure 3-8 shows the installation.

Fig. 3-8: Hot test installation

Observations:

Out of these tests corrective equations were developed by plotting reference British Standard thermometer readings against thermocouple measured temperatures. Each thermocouple had an associated equation. Comparison between linear and polynomial trends were undertaken and showed that a linear regression was sufficiently accurate to be applied. For each new value read by the thermocouple, the correct value was determined by its equation.

Errors were quantified statistically by using the coefficient of determination, R2, mean bias error, MBE, root mean square error, RMSE, as well as Skewness and Kurtosis of the error histograms and showed acceptable margin of errors. These statistical factors are further explained in Chapter 4.

Thermocouple positions in the collector

The calibrated thermocouples were used to monitor water temperature at different positions in the collector. A good distribution of the thermocouples in an inclined ICS-SWH is essential to determine the temperature profile inside the collector as stratification causes a variable temperature distribution inside the water tank. Past studies on ICS-SWH by Grassie et al (2006) suggested a positioning scheme of thermocouples in ICS-SWH. Temperature profiles observed by Grassie et al (2006) showed that further thermocouples should be added at the collector’s extremities to evaluate accurately phenomenon occurring in these zones. A new thermocouple distribution was therefore developed. Thermocouples were doubled at the top and bottom part of the middle acrylic clear tube. Both distributions are represented in Figure 3-9 below.

Fig. 3-9: Thermocouple positions and volume control associated, a: Aluminium collector, b: Stainless-steel Collector (Junaidi et al (2005)).

Control volumes, represented by dashed lines, were assigned to each of the thermocouples in order to effectively evaluate an average temperature for the water tank. The temperature profile in the SWH could then be developed using monitored temperature data.

Thermocouple’s inserts and positions

Clear acrylic tube inserts were used in order to provide support for the thermocouples. The high resistance to heat distortion and simplicity to insert thermocouples along acrylic clear tubes made it the best option for this application. Thermocouples were running through the acrylic plastic tube inserts with multiple slots to expose the thermocouple tips to the water as shown in Figure 3-10. Tips were fixed in the slot by silicone.

Fig. 3-10: Acrylic plastic tubes inserts with thermocouple slot

Acrylic plastic tubes were placed in the collector through three pipes previously integrated in the collector design as shown in Figure 3-11.

Fig. 3-11: Acrylic plastic tube inserts in pipes

Positioning of thermocouple tips in the collector

The positioning of thermocouple tips might affect the readings if the thermocouples appear to be in the flow regime as shown in Figure 3-12. Acrylic tube inserts were turned to ensure that the tips of the thermocouples were positioned down the central plane. This was identified as a potential error score when performing a critical review of previous test regimes employed in ICS-SWH development.

Fig. 3-12: Assumption of thermocouple position in the SWH

#### The electrically heated silicone rubber pad

An electrically heated silicone rubber pad was used to control power input simulating the distribution of solar radiation on the top surface of the collector during laboratory tests.

Energy distribution of the electrically heated silicone rubber pad

The heat distribution was assumed to be uniform on the collector surface, however, due to the seasonal variance in sun elevation and positioning, the distribution of solar radiation on the collector surface is non-uniform. All heat losses due to conduction were ignored during laboratory experiments. Energy distribution of the electrically heated silicone rubber pad is represented in Figure 3-13.

Fig. 3-13: Energy distribution of the electrically heated silicone rubber pad

Optimising the contact between the electrically heated silicone rubber pad and collector surface

Aluminium has good heat absorption properties as well as heat transfer properties. However, the contact between the electrically heated silicone rubber pad and the top surface of the collector should have minimum air gaps in order to maximise heat transfer. In order to compare with the methodology used by Grassie et al (2006), tests reproducing the same conditions were conducted using silicone nodes to fix the electrically heated silicone rubber pad to the collector’s top surface. Figures 3-14 and 3-13 show the surface of the pad after the experiment.

Fig. 3-14: Absorber sheet of the ICS-SWH

Fig. 3-15: Silicon paste

The adherence between the electrically heated silicone rubber pad and the collector’s surface was not optimal and therefore affected the heat transferred to the water. InfraRed Thermographic images of the pad were taken before removing the silicone node using a FLIR ThermaCAM thermal camera. Silicone and non-silicone surfaces were pictured in order to evaluate the effect of silicone on heat distribution and are represented in Figures 3-16a and b. While a uniform flux through the heating pad was expected on both sides, colder spots observed at various positions on the silicone side of the pad indicated an uneven heating pattern and uniform heat distribution to the non-silicone side of the pad.

Fig. 3-16: Heating pad thermographic images: a. Silicone side (heating side), b. Front side, Scale: (C

Figure 3-17a and b showed a more detailed picture of the uneven heating and cooling pattern of the silicone sided pad. The silicone retains heat when cooled and acts as insulation when heated.

Fig. 3-17: Heating pad thermographic images: Hot spots (a) and cool spots (b) represent the silicone welds. Scale: (C

In order to improve the initial heating methodology the silicone nodes were removed and replaced by heat sink compound paste; improving the overall heat transfer between the two surfaces by two means.

First, a uniform layer of the compound could be applied over the electrically heated silicone rubber pad attached to the collector top surface, thus providing a more uniform heat distribution and decreasing air interstices between the two surfaces. A second key factor was the higher thermal conductivity of the heat sink compound of 0.9 W/m.K compared to the silicone sealant (0.2W/m.K) resulting in a 77% improvement in heat transferred to the collector.

The electrically heated silicone rubber pad can withstand exposure temperature of up to 230(C and has a high emissivity of value 0.86. The fibreglass reinforced silicone rubber layers sandwich a pre-formed heating element made from fine resistance wires. The silicone rubber resistant heating pad dimensions were 1000 ( 960mm.

#### Data Loggers

Grant Instrument Squirrel 2020 series, type 1F8, data loggers were used for recording temperature. In the presence of a temperature difference between the junctions of the K type thermocouple a small temperature dependent current flows around the circuit. The measured voltage is converted to a temperature reading through the use of the digital data loggers using a polynomial relationship for current conversion to temperature defined by the British Standards (BS EN 60584.1). The 12 Bit data loggers have a sensitivity specification of 0.1(C.

Pyranometer

A Kipp and Zonen BF3 pyranometer was used during the field experiment to measure hourly horizontal global solar radiation in W/m2, received by the ICS-SWH. It consists of an array of photodiodes with a computer-generated shading pattern to measure incident solar radiation mounted on a base covered by a hemispherical glass dome. Incoming solar radiation lights the photodiodes converting it to a voltage proportional to the irradiance on that surface which is then read by the computer. Based on Chapter 2, a 45( inclination of the ICS-SWH was used for field tests. The “solar radiation and daylight Model” developed by Clarke and Muneer (2008) was used to get adjusted solar radiation for the required inclination.

### Experimental considerations

The aim of this section is the identification of the errors due to the assumptions and test regime that have been made during the experimentation phase.

Heated surface

The heat distribution of the electrically heated silicone rubber pad was assumed to be uniform on the top surface of the heater. All heat losses due to conduction were ignored during the laboratory experimental tests, however the effects of the heat losses from the electrically heated silicone rubber pad to the ambient air, the thermal capacitance of the water storage unit, the glass reflectivity and all other associated losses were taken into account.

Leakage and pressure inside the collector

The extremities of the pipes from which the acrylic plastic tubes with thermocouples were inserted were sealed with silicone to avoid any leaks. This might have caused minor problems due to the build up of pressure inside the collector and thus expansion of the collector and/or drive the water at the top of the pipes. An expansion water tank was installed on top of the inlet pipe to overcome such problems.

Departure temperature

Tests were carried out for different controlled heat fluxes provided by the electrically heated silicone rubber pad. In order to achieve comparable results starting water temperatures had to be the same for each experiment. Therefore, water in the collector was purged and replaced by fresh water at approximately 14(C after each experiment.

Wind data

Wind speeds were recorded hourly by an anemometer for field tests; however, only an average wind speed for the location was utilised in calculations as directions were not recorded. The location of the ICS-SWH was partly sheltered from wind, therefore decreasing its effect on the glass cover.

## Laboratory experiments

### Experimental set up

The equipment set up for the laboratory tests attempted to replicate the previous experimental schemes of Grassie et al (2006) in order to compare their respective performance and is described in this section. A total of 22 thermocouples were used to measure water temperature inside the collector as shown previously in Figure 3-11. Ambient temperatures inside the laboratory were recorded by two thermocouples while three others were placed on the glass cover. The electrically heated silicone rubber pad was designed to simulate a constant and uniform heat flux over the flat plate collector reproducing Edinburgh solar conditions. A variac transformer controlled the power supply to obtain a measured amount of heat. Tests were carried out for heat fluxes from 100 to 400 W/m2 with increasing intervals of 50 W/m2 at different angles including 0 – 30 – 35 – 45 – 60(. Temperatures were recorded at 10 minute intervals over 24 hours, giving time to reach a state of quasi-equilibrium. The test rig is shown in Figure 3-18 with the circuit diagram of the electrical equipment for control and measurement of the heat flux in Figure 3-19.

Fig. 3-18: Test rig with control and measurement equipment

Fig. 3-19: Circuit diagram for control and measurement of the heat flux

### Experiment results

#### General findings

The experimental data obtained replicated and validated Grassie et al’s (2006) work on stainless-steel ICS-SWH. Equilibrium was experienced after a period of 24 hours when the peak value of mean water temperature was achieved and all the input heat flux balanced with net losses. At this stage the water tank temperatures and collector efficiency tended to a constant value resulting in an asymptotic shape in their profiles. Every heat flux value has an associated water temperature when equilibrium is reached. The higher the heat flux imposed, the higher the temperature reached by the collector but the lower is the overall efficiency as this is the ratio of power output to power input.

In accordance with the results of Grassie et al (2006), an increase of the temperature stratification with time was observed in the ICS-SWH. The system behaviour also varied with the angle of inclination. Grassie et al (2006) showed that system performance differs at various inclination angles and showed that thermal optima increased by increasing angle of inclination. However, it was suggested that an angle of 45( gave the best overall results when analysing temperatures reached over time, thus achieving high efficiencies. Results of the research confirmed that the suggestion of an inclination angle of 45( for the ICS-SWH position was appropriate for Edinburgh. Further experiments at this inclination showed that the ICS-SWH can work successfully in a Scottish climate.

#### Aluminium ICS-SWH stratification

Stratification in a water tank is an essential factor for good performance of an ICS-SWH. It refers to the degree of temperature difference between the top and the bottom portions of the collector. In order to determine dimensionless stratification, experimental temperature profiles were scaled and hence the ratio Th / Tbottom was introduced where Th is the local and Tbottom is the minimum recorded temperature in the water tank. Stratification profiles for different hours are plotted for a heat flux of 200W/m2 in Figure 3-20. The overall collector temperature increases with time until reaching steady-state. The first three hours show a rapid increase in temperature stratification, decreasing later with time until reaching equilibrium.

Fig. 3-20: Temperature stratification profile for a 200W/m2 heat flux

Water at a given temperature will settle down at an appropriate height in the ICS-SWH in accordance with the prevalent density of the fluid. Hot water of low density will naturally sit in the upper layers while cold water of high density will drop down to the bottom layers. During the first three hours of the charging process, high temperature stratification occurs in the ICS-SWH.  With time, the temperature of the upper layers is established and reaches an equilibrium which results in the lower layer achieving a similar temperature. This therefore decreases the density gradient inside the ICS-SWH. A temperature stratification profile is thus built up.

This variation in density results in differential buoyancy forces in the fluid causing convection by gravity. Pressures increases with depth, therefore the pressure within the collector will experience different pressures at the top and bottom, with the pressure on the bottom being higher. This difference in pressure causes an upward buoyancy force. The buoyancy force,, is thus the difference between the forces at the top and bottom in the collector for one square meter and can be expressed as below:

(3.1)

Where   is the density of the fluid at the bottom of the collector (kg/m3)

is the density of the fluid at the top of the collector (kg/m3)

is the vertical length from top to bottom of the collector (m)

is the standard gravity of  9.81N/kg

Resulting buoyancy forces within the collector were then calculated. During the charging period forces increase within the cavity from 3.2N to 8.3N generating buoyancy driven flows within the cavity. This resulted in an increase in thermal stratification within the cavity from 2.6(C to 3.6(C. With time the temperature difference between top and bottom decreases. This reduction can be associated with a decrease in buoyancy forces operating within the cavity therefore reducing fluid motion and natural convection occurring in the collector. After 16hrs, the temperature gradient decreased to 1.9(C associated with a buoyancy force of 4.6N. These results are presented in Figure 3-21.

Fig. 3-21: Buoyancy forces with time

The stratification profile was plotted for an average day length of eight hours of ICS-SWH operation for different wattages. One such profile is shown in Figure 3-22. A definite relationship between the temperature at any point of the collector and the applied heat flux was observed. The higher the heat flux imposed the higher the water temperature ratio Th / Tbottom.

Fig. 3-22: Temperature stratification profile after 8 hours of operation

Temperatures are thus dependent on the longitudinal position within the collector, applied heat flux, and time. A polynomial function for the stratification profile for each hour was then developed taking heat flux and longitudinal location in the collector as the main parameters.

### Comparison of past and current research

A comparative analysis between the stainless-steel ICS-SWHs previously developed by Grassie et al (2006) alongside the newly developed aluminium ICS-SWH was performed in order to validate experiments and to show the benefit of the new ICS-SWH. The methodology adopted in both studies were first compared followed by comparisons of experimental results.

#### Test setup comparison

Methodologies adopted in the research were compared with those used by Grassie et al (2006) to give a viable comparison. The newer collectors were designed and manufactured with 3mm thick aluminium sheets as compared to the 1.5mm thick stainless-steel 304-2B ICS-SWH of the same overall dimensions. Grassie et al (2006) developed two ICS-SWHs; one with and one without fins.

Twenty-two K-type thermocouples were calibrated and used to monitor the temperature profile inside the aluminium collector compared to twelve thermocouples used in the stainless-steel collectors. Information on the calibration of the thermocouples was not available for the stainless-steel ICS-SWH experiments.

In order to demonstrate the influence of the number of thermocouples on the accuracy of results, a first set of calculations using Grassie et al’s (2006) thermocouple positions for the aluminium collector was implemented. Calculations were then repeated but taking into account the 22 thermocouples. It was established that the number of thermocouples did not influence the overall efficiency results.

The second comparison consisted of the methodology for calculating efficiencies. The heat capacity (Cp) and density (() of the water were assumed to be constant by Grassie et al (2006) contrary to the more accurate method adopted in this research where Cp and ( were calculated as a function of the water temperature in the collector. An accuracy difference of 1% on the overall efficiencies was found by comparing the two methods.

Finally, materials used to attach the electrically heated silicone rubber pad to the collector top surface were different. Silicone was used by Grassie et al (2006) rather than a heat sink compound. Two tests were carried out using both materials in order to compare the conductivity of the two materials resulting in a efficiency difference of 1% between the two methods. Other parameters which might have affected the accuracy of the results were the calibration of the thermocouples and data logging equipment.

Based on this methodology the thermal performances of the two finned ICS-SWHs and benefits of using fins were assessed, compared and adjusted. Results are reported in the next section.

#### Stratification analysis

The first comparison consisted of a stratification analysis. A dimensionless study of water temperature according to the distance from bottom to top portions of the collector was developed with the aim of comparing the thermal stratification of both ICS-SWHs. Dimensionless temperature of ratio “” was plotted in Figure 3-23 against the dimensionless distance ratio “” where  is the water temperature at the local point ((K),  is the water temperature at the top of the collector ((K),  is the local length in the collector (m),  is the total length of the collector (m).

Figure 3-23 a and b confirm findings from section 3.2.2.2 for the aluminium material only. It validates that the higher the heat flux applied the higher the stratification in the ICS-SWH and that the longer the exposure time is the lower is the stratification due to the buoyancy. These findings are consistent with those of Grassie et al (2006).

Fig. 3-23: Dimensionless temperature “Th/TH” vs dimensionless distance “h/H” at 45( inclination, a: 100W/m2 heat flux input, b: 400W/m2 heat flux input

Another important finding from this figure is the effect of the collector material on stratification. Steeper stratification curves were found in the stainless-steel ICS-SWH compared with the aluminium profiles demonstrating a better mixing in the latest ICS-SWH. This decrease in stratification is explained by the higher conductivity of aluminium material allowing a more rapid transfer of heat from the top to bottom water layers. Figure 3.-24 support this finding by depicting the rise in temperature registered by the thermocouples placed at the top and bottom in the stainless-steel and aluminium ICS-SWH.

Fig. 3-24: Water temperature profiles of finned aluminium and stainless-steel ICS-SWHs at 400W, 45( inclination.

Higher water stratification was achieved by the stainless-steel ICS-SWH compared to aluminium with 9.0°C  and 4.5°C difference respectively from the bottom to top of the collector after an exposure time of eight hours. The aluminium temperature profile clearly shows that the heat transferred to the water was improved and generated higher overall water temperatures.

These results indicate that stratification depends upon the incident solar radiation (heat flux applied to the collector surface), the exposure time and collector material for a given angle of inclination of the collector.

#### Benefits of introduction of fins in the collector design

In order to quantify the benefit of integrating fins in the collector, a comparison of the actual rise in temperature of the finned aluminium, finned and un-finned stainless-steel ICS-SWHs was used. Figure 3-25 compares the results obtained from preliminary experiments where .  is the initial mean water temperature and  is the mean water temperature at any time t.

A rise in temperature of 19.2(C, 16.8(C and 13.8(C was observed after eight hours of exposure time at 200W/m2 for the finned aluminium, finned stainless-steel and un-finned stainless steel ICS-SWHs respectively. This corresponded to an improvement of 18% by using fins in the stainless-steel ICS-SWH, and an additional 13% improvement using the more conductive aluminium.

Fig. 3-25: Water temperature profiles of finned aluminium, finned and un-finned stainless-steel ICS-SWHs for eight hours of exposure time at 200W.

In order to support the results identified above the overall water temperature of the un-finned stainless-steel collector was plotted as a function of the finned stainless-steel ICS-SWH in Figure 3-26., and as a function of the finned aluminium ICS-SWH in Figure 3-27. These scatter plots have the very specific purpose of demonstrating how much the “fin” affects water temperature achieved in the collector. It is apparent from Figure 3-26 and 3-27 that the finned heaters outperform the un-finned by achieving a higher temperature rise  illustrated in Figure 3-26 and 3-27 by the deviation from the “one to one” straight line relationship. Figure 3-26 and 3-27 also shows that over time, data points converge; approaching to the “one to one” straight line relationship. Gradually, un-finned and finned water temperature in the collector tends to reach the same value; approaching an equilibrium temperature observed for the 100W/m2 heat flux profile.

Fig. 3-26: ICS-SWH water temperature increase: un-finned versus finned stainless-steel

Fig. 3-27: ICS-SWH water temperature increase: un-finned stainless-steel versus finned aluminium

These findings suggest that incorporating fins in the collector results in an increase in heat transfer, and that using aluminium generates higher overall water temperatures as shown in Figure 3-26 and 3-27. In a real world application water will be regularly drawn from the ICS-SWH, not allowing enough time for the water to achieve equilibrium temperature, early differences in temperature rise is critical for the good performance of the ICS-SWH.

#### Efficiency improvement

Taking into account all the parameters discussed in section 3.2.3.1, efficiencies were calculated by the following equation and then corrected. The collector efficiency is the ratio of the bulk heat collected to the heat available as shown in equation 3.2.

(3.2)

Where  is the heat collected at each control volume (W/m2)

is total irradiation from the heating pad (W/m2)

Also expressed as

With 	(3.3)

Overall efficiency:				(3.4)

Where  is the control volume associated of the thermocouple “i”	(m3),  is the heat flux applied to the system (W),  is the specific heat capacity of water associated with thermocouple temperature (J/kg.(K),  is the water density associated with the thermocouple temperature (kg/m3), 	 is the temperature difference between t=j and t=0s ((K) and  is the time step (s).

To assess the improvement in efficiency of the new aluminium ICS-SWH results of the above calculations are shown in Figure 3-28.

Fig. 3-28: Aluminium and stainless-steel ICS-SWH efficiency comparison at 45 degree inclination, 100W/400W

Figure 3-28 illustrates two phases in the efficiency curves. Phase one shows a fast increase in efficiency followed by a regular decrease in phase two. This trend is due to the thermal mass of the system. It corresponds to the heat stored in the collector material and the water for a given power applied to the system. Figure 3-28 shows that a longer period was needed for lower heat fluxes as it takes longer for the material to charge. The charging stage, associated with the first phase is then dependent on the heat flux applied. The same figure outlines that the thermal mass of the system is strongly dependent on the type of material used for the collector. The aluminium collector has a heat capacity of 17.2 kJ/K compared to 13.3kJ/K for the stainless-steel. The 23% difference explains the fact that the aluminium collector needs more time to charge for lower heat flux and vice-versa.

Overall efficiencies obtained from the preliminary analysis for aluminium and stainless-steel ICS-SWH are presented in Table 3.3. Total efficiencies vary according to the heat flux in a similar way to that described by Grassie et al (2006). The higher the heat flux applied to the system, the lower the overall efficiency.

Table 3-3: Stainless-steel vs aluminium overall efficiencies for different heat flux: Note laboratory tests

| Collector type | Heat flux applied | Average overall efficiency |
| --- | --- | --- |
|  | 100W | 200W | 300W | 400W |  |
| Aluminium | 77% | 77% | 66% | 63% | 71% |
| Stainless-steel | 68% | 68% | 63% | 62% | 65% |

It was also identified that global efficiencies for the aluminium collector were higher at all heat input regimes compared to stainless-steel. A drop in efficiency was noted between 200W/m2 and 300W/m2. Tests carried out for 250W/m2 showed an intermediate value of efficiency.

### Discussion of laboratory testing

The purpose of this section was to determine whether the performances of an ICS-SWH using aluminium as a material were improved by comparison with a previous study by Grassie et al (2006) utilising a stainless-steel construction device.

This chapter sets out adjustments in the methodology adopted by Grassie et al (2006) in order to make an appropriate comparison between the two ICS-SWHs. Observations showed that a generally more accurate and rigorous methodology was adopted in the experiment of the aluminium ICS-SWH.

The experimental results clearly demonstrated that using aluminium generated higher overall collector water temperatures and improved heat transfer to the water. The stratification analysis indicated that this depends upon the incident solar radiation, the exposure time and collector material, given a constant angle of inclination of the ICS-SWH.

Findings suggested that incorporating fins in the collector resulted in an increase in heat transfer of 18% in the stainless-steel ICS-SWH. Using a more conductive material such as aluminium made an improvement of 13% in water temperature. An overall increase in the aluminium ICS-SWH efficiency of 6% was found by comparing performances of both ICS-SWH over an eight hour time period.

The benefit of selecting aluminium for the ICS-SWH was clearly supported by the current findings showing it out-performing the stainless-steel ICS-SWH. Although the collector was tested in a laboratory with calibrated instruments, the actual performance of the ICS-SWH in real weather conditions would yield important results on assessing the viability of the aluminium ICS-SWH. There was therefore a strong imperative for conducting field tests with the aluminium ICS-SWH.

## Field experiments

To investigate the influence of Scottish weather conditions on the performance of the aluminium ICS-SWH, extensive field measurements were conducted in Edinburgh during the summer of 2007.

### Experimental test set up

The test rig was located on the roof of Napier University at 15.5m above ground-level or 113m above sea-level. Due to technical constraints the ICS-SWH was placed facing 143 degrees from north. The electrically heated silicone rubber pad was replaced by a black paint applied to the absorber plate to improve the solar radiation collection. Figure 3-29 shows the cross-sectional representation of the field tested ICS- SWH while an illustration of the adopted tests rig is shown in Figure 3-30

Fig. 3-29: Cross-sectional representation of the field tested ICS-SWH

Fig. 3-30: Experimental test rig

A simulated roof-structure was used to insulate the sides and back of the ICS-SWH. It protected the ICS-SWH from the effects of weather by creating a micro-environment and by decreasing the heat losses from the back of the ICS-SWH. Kingspan insulation closed-cell polyurethane material was used partially to insulate the bottom of the ICS-SWH and the back side of the simulated roof-structure as shown in Figure 3-31.

Fig. 3-31: Back insulation of roof simulated box

Mineral fibre wool was then placed inside the simulated roof-structure and rigid insulation was sized and placed on the sides. Wood was then fixed on top of the insulation as well as a flush system on top of the collector to avoid any water ingress. Pipes were insulated in order to avoid possible freezing during cold days.  Figure 3-32 shows the final installation.

Fig. 3-32: Experimental test rig side insulation

The same 22 K-type thermocouples used for laboratory experiments were connected to a data-acquisition system to monitor the water temperature inside the aluminium collector covering middle longitudinal and lateral lines. Other thermocouples were used to record the absorber plate, the glass cover, the ambient, and the inlet and outlet water temperatures. A calibrated Kipp and Zonen BF3 pyranometer was used to record solar radiations at the location of the ICS-SWH while an average wind speed of 3.7 m/s was recorded next to the location of the ICS-SWH using a WMS302 Vaisala anemometer. This average data was taken as the reference wind speed in the study. A cold water tank was placed above the ICS-SWH to feed the collector with fresh cold water and a valve was used when draw-off of water occurred. A timer was placed to simulate water draw-off profiles. The angle of inclination of the ICS-SWH was kept at 45(, hourly radiation and ten minutes interval temperatures were recorded for an initial period of three months.

### Experiment results

#### Without Draw-Off

Field tests started on 6th June 2007 for an initial period of three months. In order to identify the performance of the ICS-SWH, data management and analysis were performed for a typical month of July. Recorded data during the period of the 11th-26th of July are represented in Figure 3-33 where Tw is the bulk water temperature, Ta is the ambient temperature, Tp is the plate temperature and Tc is the cover temperature.

Fig. 3-33: Field experiment data

Each day is characterised by a heating and a cooling profile which are dictated by solar radiation. The higher the incident solar radiation received by the absorber plate, the higher the water temperature achieved. The decrease in incident solar radiation results in heat losses from the collector to the surroundings leading to a subsequent decrease in water temperature. The gradual heating and cooling profiles seen are due to the thermal mass of the system previously introduced during the efficiency study of laboratory experiments. The thermal mass is the capacity of a material to store heat. It plays an important role in the effectiveness of the heating charge and cooling discharge operations of the collector and the amount of the stored thermal energy. The water stored in the collector accounts for most of the thermal mass of the system. The high specific heat 4.18kJ/kg.(K and moderate density of 1000 kg/m3 of the water results in a relatively high volumetric capacity of 4180 kJ/m3.(K. This shows the ability of a given water volume to store internal energy while undergoing a given temperature change. Its low thermal conductivity of 0.58W/m.(K also contributes to this effect by slowly storing or releasing heat. The collector material also contributes to the thermal mass through its moderate volumetric capacity of 2424 kJ/m3.(K, assuming the density of aluminium at 2770 kg/m3 and a specific heat of 875J/kg.(K. This results in a thermal mass of 224.7 kJ/(K for the collector.

A more detailed picture of a typical day of July is illustrated in Figure 3-34.The collector is warmed passively by the solar radiation during the day. Heat stored in the mass is retained and gradually released back during the night illustrated by the cooling discharge profile.

Fig. 3-34: One day field experiment data

Figure 3-34 demonstrates the close relationship between the absorber plate and water temperatures and supports findings on the effect of thermal mass. The absorber plate absorbs incident solar radiation during the charging operation resulting in an increase of absorber plate temperature. The absorber plate transfers the heat to the water resulting in similar temperature profiles. A decrease in incident solar radiation on the absorber plate, due to shade, resulted in a decrease in absorber plate and water temperatures. However, as the water volume retained more heat than the absorber plate, higher water temperature occurred during discharge. It was also observed that a significant decrease in incident solar radiation for a relatively long period of time during the day can lead to significant losses. However, a short time period would not affect the system considerably as shown Figure 3-34 between the hours of 12 and 16hrs.

Sky radiation effect on cover temperature

Further analysis of the cover and ambient temperatures in Figures 3-35 showed significant outcomes. It can be seen that recorded cover temperatures were lower than ambient temperatures during daytime of the 11th and 15th of July. A possible explanation for this might be that the effective sky temperature can be about 10-20 degrees Celcius below ambient temperature at ground level with clear sky conditions and close to or just below the ambient temperature during cloudy conditions. In order to assess this possible explanation the clear sky index for the location of the ICS-SWH for those dates were taken from the BADC (British Atmospheric Data Centre) and plotted against both temperatures in Figure 3-35.

Fig. 3-35: Sky radiation effect on cover temperature with kc as the clear sky index

Both days were recorded as clear sky days from the BADC (2007). The sky acts as a black body during night-time and during an early morning clear sky, resulting in a cover temperature lower than the ambient temperature. The energy network illustrating the exchanges between the cover “C” and the absorber plate “P” as well as the ambient air “A” and the “Sky” node is shown in Figure 3-36.

Fig. 3-36: Energy network for clear sky conditions

Stratification and solar radiation

In order to identify the influence of incident solar radiation on stratification the rise in temperature registered by thermocouples placed at different locations along the length of the collector is illustrated in Figure 3-37.  Strong evidence of the importance of the shading effect was found for the hours 11, 12 and 13 where a decrease in stratification rate was recorded, supporting previous findings. This is due to a sudden decrease in incident solar radiation on the collector.

Fig. 3-37: Stratification with time and solar radiation

In order to support these findings experimental temperature profiles were scaled to the ratio Th / Tbottom where Th is the local and Tbottom is the minimum recorded temperature in the water tank. Dimensionless stratification profiles for different hours are represented in Figure 3-38 for the same typical day.

Fig. 3-38: Dimensionless longitudinal stratification: Th / Tbottom versus h/L

Temperature stratification decreases gradually over night until 6am, at which time incident solar radiation starts being collected by the absorber plate. While the overall collector temperature increases from 7am to 2pm, stratification increases from 7am to 9am then decreasing later with time. This is explained by the buoyancy effect already discussed in section 3.2.2.2. From 7am high temperature stratification occurs in the ICS-SWH.  At 9am the temperature of the upper layers is established resulting in the lower layer achieving a narrower temperature range, therefore decreasing the stratification in the collector. A decrease in de-stratification rate was observed at the 11, 12 and 13hr suggesting that the collector was shaded. This is supported by a sudden decrease in incident solar radiation on the collector for this period of time shown in Figure 3-37.

Collection efficiency

It should be noted that the following procedure can be applied to ICS-SWH evaluation; however it is not truly representative of actual system performance due to its transient or dynamic nature.

The common standard procedure developed by the European Solar Collector and Systems Testing Group, ESCSTG (1989) was used to measure the effectiveness of the ICS-SWH. Assuming the collector is operating in a steady state condition, an energy balance represented by equation 3.5 enables the calculation of the rate of useful energy gain.

(3.5)

Where  is the optical efficiency (transmission-absorption product) of the single glazed float glass cover

Tw is the bulk water temperature ((K)

Ta is ambient air temperature ((K)

U is the combined collector heat loss coefficient (W/m2.(K).

is the incident solar radiation (W/m2)

Based on equation 3.2 already described in section 3.2.3.4, the collector efficiency is the ratio of the bulk heat collected to the heat available.

Using equations (3.2) and (3.5), an expression for efficiency was developed in equation 3.6 below.

(3.6)

To avoid negative values of efficiency occurring at early morning or late afternoon a critical irradiance was introduced. Negative values can occur when incident solar radiations are lower than the heat losses of the ICS-SWH. This method allowed setting the heat collection to nil in order to sustain a net energy gain.

(3.7)

As discussed by ESCSTG (1989) equation (3.6) is useful because it can be used to plot an informative efficiency curve, which predicts collector performance for any operating point.

A constant heat loss coefficient would result in a straight line if efficiency is plotted against the known operating point. Figure 3-39 illustrates the efficiency curve for the ICS-SWH experiment data. Based on equation 3.6, the heat loss coefficient of the ICS-SWH was found to be 4.5 W/m2.(K.

Fig. 3-39: Efficiency line for the ICS-SWH studied

As the temperature difference between the bulk water and ambient air increases the efficiency of collection falls. For any given operating point the efficiency could be obtained from Figure 3-39 and used to predict the thermal performance of the ICS-SWH. However, limitations occur by using this procedure for ICS-SWH as it applies (only) to diurnal system performance. This performance method is applied to the flat plate collector working in a steady state mode.

#### With Draw-Off

Field tests with draw-off were carried out for the month of August in order to identify how the ICS-SWH would operate in a building. Based on the literature review, developed in Chapter 2, McLennan (2006) water consumption for a typical day in Scotland was taken as reference for an average household of 2.44 persons. The ICS-SWH was designed as 50 litres or the consumption of one person. Therefore McLennan (2006) draw-off profiles were adjusted for one person in order to make an appropriate analysis. Due to experiment restriction caused by the low accuracy of the timer a minimum flow rate of 0.008l/m2.s was established delivering an average daily hot water consumption of 79l/day/person. McLennan (2006) and the experimental draw-off pattern established are shown in Table 3-4 below.

Table 3-4: Daily hot water demand profile

|  | Average hot water demand profile by McLennan for 2.44 person | Average draw-off profiles used in experiment assuming 1m2/person |
| --- | --- | --- |
| Hours | Litres/hrs | Litres/hrs |
| 1 | 0 | 0 |
| 2 | 0 | 0 |
| 3 | 0 | 0 |
| 4 | 0 | 0 |
| 5 | 1 | 0 |
| 6 | 1 | 0 |
| 7 | 4 | 3 |
| 8 | 23 | 15 |
| 9 | 10 | 7 |
| 10 | 6 | 4 |
| 11 | 6 | 4 |
| 12 | 4 | 3 |
| 13 | 5 | 3 |
| 14 | 2 | 1 |
| 15 | 2 | 1 |
| 16 | 1 | 1 |
| 17 | 2 | 1 |
| 18 | 4 | 3 |
| 19 | 16 | 11 |
| 20 | 13 | 9 |
| 21 | 7 | 5 |
| 22 | 9 | 6 |
| 23 | 5 | 3 |
| 24 | 1 | 0 |
| Total water consumption: | 122 Litres/day | 79 Litres/day/pers |

The flow rate achieved for the experiment of 0.008l/m2.s was found acceptable when compared with previous research of Duffie and Beckman (1991) suggesting flow rates of 0.015kg/m2.s or lower flow rates of  0.002 to 0.006 kg/m2.s recently used in Sweden. Recorded data for two typical days of August are represented below in Figure 3-40.

Fig. 3-40: Stratification in the ICS-SWH and water temperature draw-off

The manufacturing error addressed in section 3.1.1.2 concerning the positioning of the outlet pipe might affect the flow inside the ICS-SWH when cold water is introduced; however no specific problems were observed. Results showed that the low flow rate used for experiments maintained a high level of temperature stratification. A sudden drop in temperature at the bottom of the tank is recorded at peak demand hours of 19:00 and 20:00. The hot water is tapped and replaced by cold inlet water at the bottom of the collector therefore decreasing the lower tank water temperature. Strong evidence suggesting that draw-off increases the overall stratification is shown in Figure 3-40. A more detailed picture for day two encompassing an interesting set of results is shown in Figure 3-41.

Fig. 3-41: Draw-off profile and performance

It is noticed that the water collected is equal to or above the mean water temperature. This is merely due to the stratification inside the tank. The lower mean water temperature achieved after draw-off suggests once more an increase of the overall stratification in the collector. The average temperatures of the water drawn-off were recorded as 30.4(C, 36.2(C, 45.5(C and finally 39.7(C at peak demand hours of 8:00, 9:00, 19:00 and 20:00 respectively. In order to support the statement that “draw-off increases the overall stratification” of the collector stratification analysis was carried out at the two daily peak demand periods and is illustrated in Figure 3-42 and 3-43.

Fig. 3-42: Ante Meridian dimensionless longitudinal stratification with draw-off: Th / Tbottom Vs h/H

Temperature stratification decreases gradually by night until 5am. The temperature stratification then increases with time, from 6am to 11am while the overall collector temperature increases until 2pm. This increase in stratification is due to cold water being introduced at the bottom of the collector lowering bottom water temperature therefore increasing the temperature stratification inside the collector. Stratification then decreases from 12am to 4pm during which time there is no significant water draw-off. Temperature of the upper layers then starts to be established resulting in the lower layer achieving a closer equivalent temperature. The temperature stratification then increases from 5pm to 7pm due to an increase in water being used. An interesting result comes from the decrease in stratification at 8pm, despite the water being drained-off. This can be explained by the combination of the large amount of water used at 7pm and the very low or nil incident solar radiation received by the absorber plate at 8pm in August resulting in a lower top collector temperature rise.

Fig. 3-43: Post Meridian dimensionless longitudinal stratification with draw-off: Th / Tbottom Vs h/H

### Discussion of field testing

#### Without draw-off

One anticipated finding showed that the higher the incident solar radiation received by the absorber plate, the higher the water temperature achieved. It was demonstrated that the thermal mass plays an important role in the effectiveness of the system as it affects the heating charge and cooling discharge operations of the collector. It was also observed that a significant decrease in incident solar radiation for a relatively long period of time can lead to significant losses, therefore positioning of the ICS-SWH is of primary importance to achieving good performances. It was assessed the cloud cover should not be neglected as it affects the cover temperature and therefore the final water temperature output of the ICS-SWH. Finally, the common standard procedure developed by the ESCSTG (1989) applied to the ICS-SWH suggested that there was a need for new methods to predict water temperatures achieved and performances of ICS-SWH.

#### With draw-off

Results demonstrated that draw-off increases the overall thermal longitudinal stratification in the collector. The manufacturing error of the positioning of the outlet pipe showed no adverse effect on temperature stratification inside the collector. Average draw-off temperatures recorded at peak demand hours suggest that the ICS-SWH could cover 55%, 66%, 83% 72% of the hot water demand at 8:00, 9:00, 19:00 and 20:00 respectively based on a delivery temperature of 55°C. A strong relationship between water drawn-off, water temperature stratification, solar radiation and outlet water temperature achieved in the collector was reported. It was shown that the ICS-SWH maintained temperature stratification when draw-off occurred and even improved it.

## Uncertainties and errors associated with measurements

Investigating uncertainties and propagation of errors in experimental procedures is essential to determine the quality of the data presented. Any likely sources of errors or problems related to measurement may be categorised under the following two main categories: equipment error and uncertainty and operation related problems and errors. A brief analysis of both categories is detailed below.

### Equipment error and uncertainty

With any measurement there exist errors, some of which are systematic and others inherent to the equipment employed. The uncertainty in the resolution is often referred to as the accuracy of the equipment. Equipment uncertainty and error were analysed and are reported.

Temperatures in the collector were measured using K-type thermocouples. The uncertainty in thermocouple measurement after calibration was found to be (0.5(C. Uncertainties associated with calibration were neglected as accurate methods were used to define the temperature of each thermocouple. An additional uncertainty of 0.1(C was associated with data logger conversion due to its limitation in resolution.

The electrically heated silicone rubber pad and electrical equipment used in the laboratory experiment for control and measurement of the heat flux had associated uncertainties. The ammeter and voltmeter used in the laboratory were checked. Uncertainty in measuring voltage and current were found to be (3% and (1% of reading values. A wattmeter was used to check the heat flux already measured through the ammeter and voltmeter. The uncertainty in the power output associated to the wattmeter was found to be (4.5%. The uncertainty associated with the conversion efficiency from electrical to heat is difficult to assess as no technical data were provided by the electrically heated silicone rubber pad manufacturer. An overall uncertainty of (10% in applied heat flux was found acceptable.

Field experiments equipment used for control and measurements have associated uncertainties. The BF3 has an estimated uncertainty in global radiation measurement of (5W/m2 at 95% confidence limits. This suggests that 95% of individual readings will be within the stated limits under normal climatic conditions. The accuracy of the anemometer was suggested at (0.3m/s for a wind speed less than 10m/s, therefore appropriate for the ICS-SWH location. The timer used for experiments showed limitations associated with the draw off profiles. The shortest switch time was of 1 minute therefore restraining the draw-off profile able to be achieved and has an accuracy of ( 4 minutes per year.

### Operational errors

In addition to the above sources of equipment-related errors, care should be taken to avoid operational errors highlighted below:

- Operation related problems and errors

- Complete or partial shade of the BF3 from direct sunlight by buildings

- Dust, snow, dew, water-droplets, bird droppings etc.

- Incorrect sensor levelling

Processing errors, human errors or calibration errors are amongst others.

## Concluding remarks

A review of the methodology adopted during laboratory and field experiments was presented herein. An account of the laboratory experimental set up with its results was given. ICS-SWH performance was found to be enhanced by using aluminium material. Determination of stratification dependent parameters, presentably of interest to this research project was also discussed in order to model stratification for laboratory conditions. A field experiment was advised and carried out to show the actual performance of the ICS-SWH in real weather conditions. Parameters such as thermal mass of the system, incident solar radiation, cloud cover and sky temperature were found to influence significantly the ICS-SWH performance and are of high interest in order to model performance of such ICS-SWH for field conditions. Current procedures measuring the effectiveness of ICS-SWH emphasise a need to predict water temperatures and performances achieved of ICS-SWH.  It was also noted that the ICS-SWH is able to maintain temperature stratification when draw-off occurred, a crucial factor to maintain good performance of the ICS-SWH. It was also observed that draw-off actually increased the overall stratification, thus improving the overall performance of the ICS-SWH. Finally an account of uncertainties and propagation of errors through both experimental set-ups were addressed.

The work demonstrated in this chapter shows the different parameters influencing the ICS-SWH and accentuates the need for the development of a thermal program predicting actual performance of such ICS-SWH.

# MODELLING

Modelling is very useful to represent the evolution of fluid flow, temperature and stratification processes in ICS-SWHs. Micro and macro models were developed to assess these parameters. The macro model assessing fluid flow and heat transfer was developed using Visual Basic for Applications (VBA). The micro model assessed the optimum fin spacing using CFD (Computational Fluid Dynamics) Fluent 6.2 software while meshing was done using pre-processor Gambit 2.2. The macro and micro models were both used through an iterative time step scheme. Numerical calculations were developed for the macro model.

## Macro model – Thermal model

As was previously stated in Chapter’s 2 and 3, the common criterion used to measure the effectiveness of flat-plate SWH using the steady state test procedure proposed by the ESCSTG (1989) cannot be applied to ICS-SWH as this involves a transient regime. Direct comparison of measured system performances is relatively straight forward; however, predicting the performance of an ICS-SWH at another location or with a different installation configuration is more challenging.

### Purpose and Language

A macro model assessing fluid flow and heat transfer in the ICS-SWH was developed using Visual Basic for Applications (VBA). This macro model is a thermal energy simulation model which analyses combined heat flux environmental networks within the ICS-SWH. It was developed to compare the temperature variation in different ICS-SWH materials, internal water temperature and external weather conditions for a given aspect ratio. The model generates corresponding bulk water temperature in the collector with a given hourly incident solar radiation, ambient temperature and inlet water temperature; thus predicting ICS-SWH performances. Depending on the conditions applied – laboratory or field – input data will differ.

### Capabilities and Limitations

VBA is functionally rich and extremely flexible but it does have some major limitations. It extends the capabilities of Microsoft  Word or Excel through macro programming language and is widely used by solar energy professionals and engineers. It can also be used to control almost all functions of the host application (Excel, Word… functions) and the graphic interface utilisation, like menus and toolbars. VBA is similar to Visual Basic (VB). However VBA can only run via a host application making it impossible to operate as a standalone executable. Excel combines a tabular data acquisition with an inbuilt VBA. In addition to this, some functions in Excel are particularly suited for engineering modelling as described by Liengme (2003) and are available in VBA as stated by Jacobson (2001). However Excel has two major limitations as it cannot tabulate more than 65,000 rows, nor graph more than 22,000 data points. Any function of the application or even of the whole operating system is accessible to the user running a document containing VBA macros making improvements of the program possible on a continual basis as the code is accessible. This model was built from scratch hence knowledge based ownership is whole. The short training time and the lack of special licensing requirements of this kind of application make the model attractive.

### Assumptions

A number of assumptions were made in developing the macro model for instance from lack of data or in order to reduce computation. Assumptions applying to both laboratory and field conditions are expressed below:

(a) Transient performance of the system was assumed to be steady state during the small time steps chosen to solve the thermal network

(b) Thermophysical properties were taken at the film temperature based on Muneer et al (2003) water and air properties.

(c) Heat loss through the absorber plate to the glass cover was assumed to be equal to the heat loss from the cover to ambient conditions due to steady state time step.

(d) Heat flow was assumed to be one dimensional.

(e) The absorber plate and glass cover were assumed to be isothermal for the small time steps chosen.

(f) The plate temperature was started at two degree Celsius above the water temperature in order to initialise the simulation. This was later recalculated by the programme through energy balance equations.

(g) The thermal analysis was undertaken for a 45( collector inclination

(h) Dust on the glass cover was assumed negligible

#### For laboratory conditions

Assumptions made to develop the laboratory macro model are given below:

(a) The thermal capacity of the transparent cover was neglected.

(b) Wind velocity was assumed to be 0.1m/s for laboratory conditions.

(c) The sky temperature was assumed equal to ambient temperature.

(d) Stratification inside the collector was first neglected and water temperature was considered as uniform. Stratification was then modelled.

Input parameters required for the system to predict ICS-SWH performance are:

(1) Heat flux

(2) Ambient air temperature

(3) Inlet water temperature

(4) Average wind velocity

(5) ICS-SWH characteristics (materials, dimensions, etc…)

(6) Inclination angle of the collector

#### For field conditions

Assumptions made to develop the field macro model are given below:

(a) The absorber plate was assumed to have a constant rate of heat flux for the small time increments taken by the programme.

(b) An average wind velocity of 3.7m/s was used for the field experiment based on data recorded on the roof where the ICS-SWH was previously tested.

(c) Radiative heat losses from the glass cover accounted the glass cover and sky emissivities.

(d) The dry-bulb temperature for part-overcast conditions was assumed as the average between the overcast and clear sky conditions.

(e) If overcast condition data were not available then the cloud cover  was assumed as part-overcast

(f) Stratification inside the collector was neglected for field experiments; it was thus assumed that water temperature inside the collector was uniform.

Input required for the system to predict ICS-SWH performance are:

(1) Horizontal global and diffuse irradiation / Sloped global irradiation

(2) Ambient temperature

(3) Inlet water temperature

(4) Wind velocity

(5) ICS-SWH characteristics (materials, dimensions, etc…)

(6) Inclination angle of the collector

(7) Cloud cover

Clear, overcast and part-overcast conditions were differentiated. Sky conditions were set as:  	Clear sky conditions:

Overcast sky conditions:

Part-overcast sky conditions:

The more detailed and complete the weather information inputs, the fewer error sources, and thus confidence in the macro model results, might be achieved.

Effects of assumptions were carefully considered in order to ensure that the analysis was appropriate. Taking these into account, a thermal network and fundamental heat transfer analysis was developed and then coded through VBA.

### Thermal network and fundamental heat transfer analysis

      - Thermal network

The model developed differentiates between unfinned and finned, collector materials and dimensions of collectors, and was developed on a steady state approach as the water temperature does not change significantly in very short time intervals. Laboratory and field macro models have differences as they are subject to different assumptions and methods of calculations. However, the global thermal network of the ICS-SWH system will remain the same and is shown in Figure 4-1 below including the water body “W”, the absorber plate “P”, the cover “C” , the ambient air “A” and the “Sky” nodes.

Fig. 4-1: Thermal network of the system

#### Fundamental heat transfer analysis

Transient performance of the system was predicted for a 360 second time interval by solving the mathematical model consisting of energy balance equations. An iterative process was developed to solve the thermal network.

The energy balance on the absorber plate at a given instant, assuming steady state conditions, is given by:

(4.1)

at t=0 					(4.2)

(4.3)

Where  is the useful energy, G((() is the rate of incident solar radiation transmitted through the glass cover to the absorber plate,  is the energy lost from the absorber plate to the water,  is the heat loss from the cover to the surroundings,  is the energy lost from the absorber plate to the glass cover, and  is the energy lost by conduction and convection from the water to the ambient. C is the overall thermal capacitance of the system composed of , , , ,  which are the water, the insulation, the wood, the glass cover, and collector material respectively and varies for field and laboratory experiments.  is the final water temperature at t=i+1 and  is the initial water temperature at t=i.

A schematic diagram of heat flux exchanges occurring at the ICS-SWH is shown in Figure 4-2 below.

Fig. 4-2: Heat flux exchanges occurring at the ICS-SWH

Heat loss from the plate to the cover

These can be expressed by:

(4.4)

where  is the bulk emissivity defined by equation ,  is the temperature of the absorber plate,  is the temperature of the glass cover temperature,  is the overall U-value between the plate and the cover, ( is the Stefan-Boltzmann constant and  is the convective heat transfer coefficient between inclined parallel plates with a slope ( from the absorber plate to the glass cover. Based on the work of Hollands et al (1976) the following relationship of for inclined cavities was developed:

(4.5)

Where  is the thermal conductivity of air at film temperature and L is the characteristic length. The notation * implies that, if the quantity in brackets is negative, it must be set equal to zero.

Heat loss from the cover to the surroundings

Losses to surroundings will differ whether the models compute laboratory or field conditions. Both are expressed below respectively:

Laboratory conditions:

(4.6)

Field conditions:

(4.7)

where  is the external convection from the glass cover to ambient,  is the sky temperature,  is the ambient temperature, is the glass cover emissivity and  is the bulk emissivity of equation where is the emissivity of the sky.

The following correlation was suggested by Duffie and Beckman (1974) for convection occurring on a collector surface where  is the wind speed.

(4.8)

According to CIBSE guide A (2006), a value of 0.1m/s of  can be used to represent convective velocity in a closed room adequate for laboratory tests. A value of 3.7m/s, based on experimental observations,  for field tests based in Edinburgh was assumed.

As stated in the literature,  is the sky temperature and is assumed equal to  for laboratory conditions. However, for field tests the sky is acting as a black body during night and during clear sky conditions in early morning.

The sky temperature was then determined by using the expression developed by Berdahl and Martin (1984) in equation (4.9) below where the sky temperature is related to the dew point temperature, , ambient temperature, , and time relative to midnight, .

(4.9)

The sky emissivity was calculated by integrating Cucumo et al’s (2006) equation (4.10) of clear sky emissivity, , into Santamouris  and Asimakopolous’s (1996) equation (4.11) for sky emissivity in the transparency window,.

(4.10)

With

Where  is the atmospheric emissivity in the transparency window for clear sky condition and  is the global emissivity.

The sky emissivity in the transparency window,, was then calculated by using the final expression by Santamouris  and Asimakopolous (1996) expressed below:

(4.11)

Where n is the total opaque cloud amount; 0 for clear sky and 1 for overcast sky.

A bulk emissivity,, taking into account the sky and glass cover emissivity of equation   was then introduced to calculate the radiative heat losses from the glass cover to the surrounding for field experiments.

Dew-point and ambient temperatures relationship were developed for Edinburgh, based on one year data from the British Atmospheric Data Centre (BADC). This data is plotted in Figures 4-3 and 4-4 from which the following relationships were developed for the different types of sky.

For clear days: 			(4.12)

For overcast days: 			(4.13)

It was assumed that part-overcast dew-point temperature was the average between clear and overcast conditions resulting in a dew-point expression below:

(4.14)

Fig. 4-3: Dew-point and ambient temperatures relationship for clear days

Fig. 4-4: Dew-point and ambient temperatures relationship for overcast days

Heat loss from the absorber plate to the water

The heat transfer to the water is mainly a convective process thus conduction was neglected. The heat loss from the absorber plate to the water is expressed below:

(4.15)

where  is the temperature of the absorber plate,  is the water temperature at t = i,  is the overall U-value between the absorber plate and the water. A Nusselt expression for trapezoidal-shaped ICS-SWH based on Fuji and Imura (1972) and adapted by Cruz et al (1999 & 2002) to evaluate  expressed as:

(4.16)

Where  and,  for Edinburgh conditions,  is the thermal conductivity of water at film temperature and L is the characteristic length. A visual description is shown in Figure 4-5 below.

Fig. 4-5: Geometric parameters of the ICS-SWH (blue nodes denote fluid temperature measurements locations)

Heat loss from the water to the ambient

(4.17)

where  is the water temperature at t = i,  is the ambient temperature and  is the overall U-value between the water to the ambient through the box, developed as:

(4.18)

Whereis the resistance of the insulation material which will vary between laboratory and field installations, and  is the resistance occurring at the box surface in contact with the wind.

Heat loss from the fins to the water

The inclusion of extended heat transfer surfaces (fins) into the design resulted in an increase in heat transfer to the water. Ideally the fin material should have a large thermal conductivity to minimize temperature variations from its base to tip. Four fins of straight, rectangular uniform cross sectional area were used for the design. Each fin was attached to a base surface of temperature called plate temperature and extends into fluid temperature  as described in Figure 4-6.

Fig. 4-6: Straight rectangular fins of uniform cross section and energy balance for an extended surface

Based on the work of Incropera and Dewitt (2001), a new model was developed using an elemental strip method to determine the heat transferred from the fin to the water assuming an adiabatic tip condition (): . The fin temperature distribution along the length  was determined by the following formula:

(4.19)

Where

= cross sectional area ()

= perimeter

= strip position

d = depth of the fins

The fin heat transfer rate  per strip can be expressed as:

(4.20)

Where  fin area

number of fins

strip length taken equal tofor modelling.

The heat transfer to the water is mainly a convective process. Muneer et al (2003) used the equation of Churchill and Chu (1975) incorporating the following regression assuming a uniform heat flux:

(4.21)

Where  with as the inclination angle of the collector and d as the depth of the fins.

The effective length of the fin was defined when 90 percent of the actual  was achieved - as only 90 percent of the heat was assumed to conduct through the fins and is represented in Figure 4-7 below.

Fig. 4-7: Dimensionless fin temperature versus fin length

The total heat transferred through the fins to the water  was calculated using the effective length of the fin. The quantity  , expressed below was calculated by adding up the fin heat transfer rate  per strip until reaching the limit of effective length.

(4.22)

An improvement factor (IF) was introduced representing the improvement achieved by using fins in the ICS-SWH over an un-finned collector and is expressed in equation 4.23 below.

(4.23)

Calculation of the bulk water temperature

Using the equations developed above, an iterative computer program was developed using VBA with initial conditions of  and  set as:

Using equations (4.2) and (4.3), expressions for  and  for t=0 were developed below in equations (4.24) and (4.25). The glass cover temperature at t=0 is a function of the assumed value of absorber plate temperature.

for laboratory conditions		(4.24)

for field conditions

(4.25)

Iterations were made until a balance was obtained between heat losses. The program finally output the glass cover temperature ‘’ and the absorber plate temperature ‘’. Heat fluxes in the network are calculated in the macro and using equation (4.1) a transformed equation (4.26) can be developed to calculate the water temperature rise:

(4.26)

An interval of one hour was taken to display results. After each interval the value of the cover, absorber plate and water temperature were calculated and used as the input for the next time step. The cycle was repeated for 24 hour time increments.

If the option “NO” fins is activated, then  is automatically set to zero, then fins are not taken into account into the calculations.

### Modelling stratification for laboratory conditions

Stratification in a water tank is an essential factor for the good performance of an ICS-SWH. This section explores the modelling of stratification inside an aluminium ICS-SWH for laboratory conditions.

Water temperatures within the collector were observed, in Chapter 3, to be dependent on the longitudinal position, imposed heat flux, and exposure time. Using experimental data, a polynomial function for the stratification profile at each hour was developed using heat flux and longitudinal position in the collector as the main parameters. In order to obtain a generalised equation for any heat flux, dimensionless temperature,( , and dimensionless length,, were calculated and plotted for each temperature measurement location for the aluminium ICS-SWH on an hourly interval. This is shown in Figure 4-8.

Fig. 4-8: Dimensionless temperature stratification after 8 hours

Polynomial functions were developed from Figure 4-8 for each wattage as defined below:

(4.27)

A single function was then developed incorporating the change of stratification with position and heat flux. The following equations were developed to produce a temperature stratification profile for an average eight hour day. Polynomial functions for heat flux of 100, 200 and 400W/m2 are expressed below:

(4.28)

(4.29)

(4.30)

A final overall expression was then developed for each hour as a function of the heat flux input and the longitudinal position in the collector. The expression for the stratified temperature at the end of eight hours of operation is given as:

(4.31)

Where a, b and c are the variation of the polynomial coefficient with heat flux for each hour. Coefficients were noted and modelled in a more generalised function and are provided below:

(4.32)

(4.33)

(4.34)

The same approach was used for each hour.

Using the previously developed macro model for laboratory conditions; polynomial functions were added to the macro model to compute water temperature stratification with height. The initial laboratory macro model was able to generate corresponding bulk water temperatures in the collector with a given hourly incident solar radiation, ambient temperature and inlet water temperature.

The new model was able to compute the bulk water temperature variation in different ICS-SWH collectors for a given aspect ratio and to evaluate temperatures at various points in the collector (temperature stratification) based on the mean water temperature given by the macro model and the total time of exposure.

Results comparing computed with experimental stratification are discussed in section 4.1.7.2.

### Digital simulation flow chart

### Computational and experimental data comparison

#### Laboratory results

Results for finned collectors

Figures 4-9 and 4-10 show the simulated heat transfer rate through the fins and the fin temperature through the fin length respectively. The fins were used to enhance heat transfer between the material and the adjoining fluid. The heat transfer rate was increased by employing different fins configuration as demonstrated in Figure 4-9. The thermal conductivity of the fin material has a strong effect on the temperature distribution along the fins (Figure 4-10) and therefore influences the degree to which the heat transfer rate is enhanced as shown in Figure 4-9. Ideally the fin material should have a large thermal conductivity to minimise temperature variations from its base to its tip.

Fig. 4-9: Simulated fin heat transfer rate

Fig. 4-10: Simulated fin temperature drop where  is the excess temperature achieved assuming 90% of heat is conducted through the fins.

Fin length effectiveness, and consequently heat transfer rate are enhanced by choosing a material with high thermal conductivity; such as aluminium. It was also enhanced by increasing the thickness of the fin, increasing at the same time the surface in contact with water. The optimum effective length of the fin was defined earlier when 90 percent of the actual  was achieved. The optimum effective length for the aluminium collector fin of 3mm and 1.5mm thickness, and stainless-steel of 1.5mm thickness were found to be 33.67, 31.50 and 12.62mm respectively; equating to an effective fin utilisation of 67.3%, 63% and 25.3%, based on their respective optimum effective length.

Similarly, a higher fin heat transfer coefficient is achieved using the higher conductivity material and greater material thickness. Indeed, by increasing the thickness a greater amount of heat was transferred through the fins’ length to achieve improved rates of heat transfer to the bottom of the collector as shown in Figure 4-11.

Fig. 4-11: Simulated fin heat transfer coefficient

Results showed that the higher the heat flux applied to the system, the higher the fin heat transfer rate achieved. However, the fin heat transfer rate decreases along the length until reaching an asymptotic value corresponding to the heat flux applied. Figure 4-12 reveals another typical trend showing that with time the fin heat transfer rate decreases. This is because with time the collector water temperature increases thus reducing heat transfer from the fins as the water approaches a temperature equilibrium with the external heat flux applied to the system

Fig. 4-12: Simulated fin heat transfer rate with time – Aluminium 3mm SWH

A fin efficiency was then calculated to evaluate the fin performance. Referring to the work of Incropera and Dewitt (2001), for a straight fin of uniform cross section and an adiabatic tip condition the fin efficiency was defined by:

(4.35)

Where .

The fin efficiencies were plotted in Figure 4-13 for the three ICS-SWH aluminium and stainless-steel fins to see the improvement in efficiency from using a higher conductivity material and by increasing the fin thickness. Higher efficiencies were achieved for the aluminium material with a 3mm fin thickness.

Fig. 4-13: Simulated fin efficiency

The improvement factor (IF) decreases with time while the water temperature increases. Indeed   decreases while   increases with time and are related to the water temperature and the IF. These results are interrelated.  A comparison between different types of fins was made for an input temperature of 22.1(C and a heat flux of 100W/m2 applied to the system. Results are presented in Table 4.1 below.

Table 4-1: Overall improvement factor for given parameters

| Material | Fin thickness, mm | Overall IF |
| --- | --- | --- |
| Aluminium | 3 | 1.14 |
| Aluminium | 1.5 | 1.10 |
| Stainless-steel | 1.5 | 1.04 |
| Unfinned | - | 1.00 |

By increasing the thickness of the fins the overall IF improved by 3.5%, while by changing the material to a more conductive material the IF improved by 5.5%. The improvement factor measuring the fin performance showed that, overall, a higher performance was achieved for the aluminium ICS-SWH with a 3mm fin thickness.

Comparison of the digital simulation and laboratory results

A comparison was undertaken between the computational results from the model and the actual experimental data. Simulated and computed efficiency of the aluminium ICS-SWH achieved with time for 400W/m2 was plotted in Figure 4-14 and show a good empirical correlation.

The comparison of the water temperatures achieved experimentally and numerically was plotted in Figure 4-15 for the three ICS-SWHs. Good correlations were observed for all the ICS-SWH types.

Fig. 4-14: ICS-SWH efficiency with time for 400W/m2 heat flux applied

Fig. 4-15: Computational and experimental comparison for 250W/m2 heat flux

Computed data were plotted as a function of experimental data in Figure 4-16 to examine the validity of the simulation. It was demonstrated that experimental and computer simulation results are in good agreement as they follow a 1:1 relationship with a 10% over prediction in the modelled value.

Fig. 4-16: Computed vs Experimental water temperatures

However, a proper validation of the results by statistical methods and extreme range tests was carried out in order to improve confidence in the findings.

Statistical measures used for evaluation of the model

In order to evaluate the performance of each set of models, the following statistical indicators were employed:

- Slope of the best-fit line

- Coefficient of determination (R2)

- Mean bias error (MBE)

- Root mean square error (RMSE)

- Skewness

- Kurtosis

The slope of the best-fit line between the computed and measured variable is desirably equal to one. Slope values exceeding one indicate over-estimation; while slope values less than one indicate under-estimation of the computed variable.

The coefficient of determination, R2, is the ratio of explained variation to the total variation. It lies between zero and one. A high value of R2 indicates a lower unexplained variation and is desirable. R2 is often used to judge the adequacy of a regression model but it should not be the only criterion for choosing a particular model.

(4.36)

Where	 = computed value

= mean value

= measured value

= number of points

The mean bias error, MBE, provides a measure of the trend of the model, whether it has a tendency to under-predict or over-predict its modelled values. Positive values of MBE indicate under estimation while negative values imply over estimation by the proposed model. A MBE nearest to zero is desired. It is given by the following equation:

(4.37)

Where = number of points

The root mean square error, RMSE, gives a value of the level of scatter that the model produces by providing a comparison of the actual deviation between the predicted and the measured values. Since it is a measure of the absolute deviation, RMSE is always positive. A lower absolute value of RMSE indicates a better model.

(4.38)

Skewness represents a measure of the lack of symmetry in a distribution.

A distribution is symmetric or normal if it looks the same to the left and right of the centre point, resulting in skewness statistic of zero value for perfect symmetry. This would indicate a robust model. A positively skewed distribution tails off to the high end of the scale while negative skew tails off the low end of the scale.

Kurtosis is defined as a measure of the degree of peakedness in the distribution, relative to its width. The kurtosis statistic will be zero for a normal distribution, positive for peaked distributions and negative for flat distributions. A peaked distribution of the errors is highly desirable. A high positive value of kurtosis suggests that there are fewer outliers in the estimation.

The six statistical indicators detailed above were used in the research to quantitatively evaluate the performance of the model. These were calculated using a macro within VBA and are summarised in Table 4-2. Extreme range tests were also used to evaluate the reliability of the laboratory macro model to predict bulk water temperature in the ICS-SWH.

Table 4-2: Statistical indicators values – Total Data

| Statistical indicator | Values |
| --- | --- |
| Slope | 1.01 |
| R2 | 0.996 |
| MBE ((C) | -0.30 |
| RMSE ((C) | 1.00 |
| Skewness ((C) | -0.79 |
| Kurtosis | 3.21 |

The slope of the best fit line between computed and measured temperature was found to be equal to 1.01 suggesting a slight over estimation of the computed variable. The high value of R2 indicates a low unexplained variation showing a good capability of the regression model. The MBE value of -0.30 shows that the model has a tendency to over predict its computed values. The low RMSE value of 1.0 shows an acceptable actual deviation. The low negative skewed distribution tends to the lower end of the scale. However, its low value of - 0.79 indicates a robust model. The positive kurtosis of 3.21 indicates a peaked distribution of the errors suggesting that there are low outliers in the estimation.

Finally extreme range tests were undertaken to show the credibility of the model. For a period of eight hours at constant heat flux of 50 and 600W/m2 good close fitting curves of computed and experimental data were achieved with very low MBE and RMSE values of -0.43 and 0.53 respectively suggesting a robust model.

Statistical and extreme range results validated the accuracy of the model to compute bulk water temperature.

      - Stratification - model results

Results

This section explores the validity of the model predicting stratification inside the ICS-SWH by comparing computed results with experimental data. The simulation was carried out for a wide range of heat inputs (50, 100, 150, 200, 250, 300, 350, 400 and 600W) for a period of eight hours simulating a typical day of operation. Computed water temperatures at any given height were plotted as a function of experimental data to examine the validity of the simulation. It was demonstrated that experimental and computer simulation results were in good agreement as they followed a 1:1 relationship shown in Figure 4-17.

Fig. 4-17: Computed vs Experimental stratification after 8 hours of operation for all heat inputs

It is observed in Figure 4-18 that variation between experimental and computed results data occurs during extended (22hr) model validation and experimental testing regime displayed graphically by a deviation from the uniform 1:1 relationship. It suggests that as temperatures increase towards boiling, bulk fluid movement is breaking down the stratification. Based on the assumption that water temperatures to be achieved in a Scottish climate are unlikely to exceed 70(C and that a typical solar heating day would be of eight hours or less make this model suitable for Scottish weather conditions.

Fig. 4-18: Computed vs Experimental stratification after 22 hours for all heat inputs

The stratification model was developed using experimental data for 100, 200 and 400W/m2. A detailed picture of the stratification model results for a heat input of 200W/m2 applied to the system for up to eight hours is showed in Figure 4-19. Each wattage followed a 1:1 relationship showing good agreement between experimental and computed data.

Fig. 4-19: 200W/m2 data - Computed vs Experimental stratification after 8 hours of operation

Statistical measures used for evaluation of the model

The previously detailed statistical indicators were used to evaluate the performance of the model to predict temperature stratification in the ICS-SWH and are summarised in Table 4-3.

Table 4-3: Statistical indicators values – Total Data

| Statistical indicator | Values |
| --- | --- |
| Slope | 1.00 |
| R2 | 0.99 |
| MBE ((C) | -0.47 |
| RMSE ((C) | 0.83 |
| Skewness ((C) | -0.17 |
| Kurtosis | 3.39 |

The slope of the best fit line was found to be equal to one suggesting no over or under estimation of the computed variable. The high value of the coefficient of determination (R2) indicates a low unexplained variation and thus good correlation. The MBE value of -0.47 shows that the model has a tendency to over predict its computed values by nearly half of one degree Celsius. The low RMSE value of 0.83 suggests a satisfactory actual deviation. The low skewness negative value of -0.17 is close enough to zero to indicate a robust model. The positive kurtosis value of 3.39 indicates a peaked distribution of the errors suggestive of fewer outliers in the estimation.

Different heat inputs outside the normal experimental range were then simulated in order to validate the model. Results for 50, 150, 250, 350 and 600W/m2 were plotted for a typical day of eight hours in Figure 4-20. The figure confirmed a good agreement between experimental and computed data following a 1:1 relationship with an MBE and RMSE of 1 and 1.4 respectively and a slope and coefficient of determination of 0.97 suggesting an under estimation of the computed variable, validating the stratification method used.

Fig. 4-20: Validation of the model - Computed vs Experimental stratification after 8 hours of operation

#### Field - model results

This section explores the validity of the model to generate and predict water bulk temperature inside the ICS-SWH for field weather conditions. Simulations were undertaken for an aluminium collector of 3mm thickness tilted at an inclination angle of 45( in order to compare computed results with experimental results undertaken on the roof of Napier University as described in Chapter 3.

Results

In accordance with laboratory computed data, the role of extended heat transfer fins was demonstrated and showed good improvement by achieving higher bulk water temperatures.

A first analysis carried out for a period of five days (11th- 15th July 2007) explores the validity of the model to predict bulk water temperature inside the ICS-SWH by comparing computed results with experimental data. Results are plotted in Figure 4-21.

Fig. 4-21: Computed and experimental data for a five day period in July 2007

Figure 4-21 shows that similar to experimental field results, computed results show that each day is characterised by a heating and a cooling profile which are dictated by solar radiation. The higher the incident solar radiation received by the absorber plate, the higher the water temperature computed. It was observed that gradual heating and cooling profiles due to the thermal mass of the system were experienced due to the consideration of thermal mass in the macro model. However, a lower cooling rate of the modelled values was observed each day. This could be explained by the propagation of errors and uncertainty by the use of regression analysis and assumed weather data; resulting in a decrease in accuracy of the model.

It was also observed in Figure 4-21 that experimental water temperature was followed very closely by predicted water temperature although it showed a slight over-estimation by the proposed model. In order to examine the validity of the simulation computed data were plotted as a function of experimental data in Figure 4-22.

Fig. 4-22: Computed vs Experimental for a five day period in July 2007

It was demonstrated that experimental and computer simulation results were in good agreement as they followed a 1:1 relationship shown in Figure 4-22. Statistical indicators were then used to evaluate the performance of the model for those five days and are resumed in Table 4-4.

Table 4-4: Statistical indicators values

| Statistical indicator | Values |
| --- | --- |
| Slope | 1.03 |
| R2 | 0.97 |
| MBE ((C) | -1.27 |
| RMSE ((C) | 2.19 |
| Skewness ((C) | 0.86 |
| Kurtosis | 0.42 |

The slope of the best fit line suggests a slight over estimation of the computed variable. The high value of R2 indicates a low unexplained variation showing a satisfactory accuracy for the regression model. The MBE value of -1.27 shows that the model has a tendency to over predict its computed values. The RMSE value of 2.19 shows an acceptable actual deviation. The low positive skewed distribution trends to the high end of the scale and indicates a robust model. The positive low kurtosis indicates a peaked distribution of the errors suggesting that there are low outliers in the estimation.

A study of the effect of wind velocity on the bulk water temperature was carried out and is illustrated by Figure 4-23 where V0, V2, V4 and V6 represents the wind velocity values of 0m/s, 2m/s, 4m/s and 6m/s respectively. The higher the wind velocity, the higher the heat losses resulting in lower bulk water temperature showing the influence of wind speed on overall performance. Thus, having accurate wind speeds would result in more accurate bulk water temperatures. The more data input, the more accurate becomes the model.

Fig. 4-23: Simulated effect of wind velocity on water temperature for a five day period in July 2007 where V0, V2, V4 and V6 represents the wind velocity values of 0m/s, 2m/s, 4m/s and 6m/s respectively

A second simulation was carried out over a period of 50 days (7th June - 27th July 2007) in order to determine the validity of the model to predict bulk water temperature for an extended period. Total computed and experimental data are plotted in Figure 4-34 at the end of the chapter.

Computed data were then plotted as a function of experimental data to examine the validity of the simulation. It was demonstrated that experimental and computer simulation results were in good agreement as shown in Figure 4-24.

Fig. 4-24: Computed vs Experimental for a 50 day period in July

The same statistical indicators were then used to evaluate the performance of the model to predict bulk water temperature in the ICS-SWH for the extended 50 day test and are given in Table 4-5.

Table 4-5: Statistical indicators values

| Statistical indicator | Values |
| --- | --- |
| Slope | 1.04 |
| R2 | 0.97 |
| MBE ((C) | -1.49 |
| RMSE ((C) | 2.22 |
| Skewness ((C) | 0.21 |
| Kurtosis | 0.16 |

The slope of the best fit line suggests an over estimation of the computed variable. The high value of R2 indicates a low unexplained variation showing a good adequacy of the regression model. The MBE value of -1.49 shows that the model has a tendency to over predict its computed values by nearly 1.5°C. The RMSE value of 2.22 shows an acceptable actual deviation. The low positive skewed distribution tails off to the high end of the scale while the positive low kurtosis indicates a peaked distribution of the errors suggesting that there are low outliers in the estimation.

Results validated the field macro model as a robust model to predict bulk water temperature in the ICS-SWH under different weather conditions.

### Error analysis

Investigating uncertainties and propagation of errors in the modelling procedure is necessary to determine the quality of the data presented. Any sources of errors may be categorised under the following two main categories: modelling uncertainties and statistical disadvantages. A brief analysis of both categories is detailed below.

      - Modelling errors

The model was coded using numerous regressions that have a band of error. The use of a series of regressions results in the propagation and intensification in uncertainty of the final result.

Other uncertainties associated with assumptions made for the different type of model and data used also intensify the uncertainty of the results. Assumption and data uncertainties were analysed and are highlighted below:

- Uncertainties of weather data recorded for simulation

- Uncertainty in material properties for calculation

- Uncertainty associated with the solar model of Clarke et al (2007) used to incline horizontal solar radiation

- Uncertainty of estimation of the total enthalpy of the water when highly stratified

- Uncertainties due to air leakage from the air cavity

- Uncertainty in calculation due to lateral stratification

      - Limitations of statistical error indices

Each statistical indicator has associated disadvantages which are important to address, some of which are described below:

- Within a dataset overestimation of one observation can over-compensate for another (underestimate), making it difficult for MBE to represent the true nature of the accuracy of the model.

-	RMSE fails to give a complete assessment of a model as only a few large errors can increase its value substantially.

-	R2 does not always measure the appropriateness of the model, since it can be artificially inflated by adding another parameter or higher order polynomial terms in the regression equation.

-	Skewness does not account for the magnitude of errors; it only gives information on the normality of their distribution.

-	Kurtosis can be very sensitive to outliers, particularly if the data set involves measured values. Thus, only a few errors in the tails of the distribution, resulting as a deviation from erroneous or irrelevant observations, can affect its value.

### Discussion of thermal models

#### Laboratory model

A macro-model for fluid flow and heat transfer was developed using Visual Basic for Applications (VBA). The role of extended heat transfer fins was modelled and showed good improvement by achieving higher bulk water temperatures. Effective fin heat transfer rates were enhanced by the choice of a material of high conductivity such as aluminium. The effective use of the fin was found to be 67.3% and 63% for the aluminium of 3mm and 1.5mm thickness and 25.3% for the 1.5mm thick stainless-steel. The fin efficiency was then calculated to measure the fin performance and showed a similar results pattern; with an improvement in efficiency achieved by using higher conductivity material. Another measure of the fin performance was introduced by using an improvement factor (IF) representing the improvement achieved by using fins in the ICS-SWH. Using a material of a high conductivity resulted in an overall improvement of 9.6%. The computational results from the model were found to be in close agreement with the experimental data. Satisfactory fitting curves were observed for the water temperatures achieved experimentally and numerically for all the ICS-SWH types. Testing of the results by statistical methods and extreme range tests validated the findings and the ability of the model to predict the water bulk temperature in the ICS-SWH.

The laboratory macro-model was able to compare and predict the temperature variation in diverse ICS-SWH configurations with different geometry, number of fins, internal temperature and constant heat flux for a given aspect ratio.

#### Stratification model

The objective of this study was to model stratification profiles with time in an ICS-SWH subjected to laboratory conditions. Three month full-scale experimental laboratory tests were employed to validate the model.

The stratification profile changes with time and therefore needed to be modelled to effectively predict the collector performance. Improvements to a previous laboratory macro-model were incorporated. This allowed longitudinal stratification of temperature within the solar collector to be determined based on the mean water temperature given by the macro model, the given heat flux and the total time of exposure.

Computational results from the model were found to be in close agreement with the experimental data with a tendency of the model to over-predict computed values by nearly half of one degree Celsius at high heat fluxes. Results were validated by using the model with wattages not used in the development phase of the program. Extreme range simulations showed the suitability of the programme to display temperature stratification.

#### Field model

Further work on the initial laboratory thermal model resulted in the development of a thermal model suitable to predict bulk water temperature in real weather conditions. Simulations for a 5 and 50 day period were undertaken. Both simulations showed that computational results were found to be in close agreement with the experimental field measurements. This statement was validated by statistical methods suggesting that the field macro-model is a robust tool to compute bulk water temperature in the ICS-SWH for any weather conditions.

This model was able to compare the temperature variation and predict the bulk water temperature in diverse ICS-SWH configurations, with different geometry, number of fins and external weather conditions for a given aspect ratio.

Although this model only gives mean values of water temperature, while in reality this varies along the longitudinal height of the collector, it gives a good estimation of the ICS-SWH performance. Results for the 50 day period also demonstrated that the simulation can be extended which could result in a useful tool to estimate the yearly performance of the ICS-SWH.

## Micro model – CFD

A Computational Fluid Dynamic (CFD) study was undertaken to model flow and heat transfer in the three-dimensional (3D) SWH geometry to provide useful information about performance of the collector and evaluate design improvements. A first analysis was undertaken for a four-fin collector designed as a mean of improving its performance.

### Purpose and fin optimisation

The CFD analysis of the ICS-SWH was undertaken in order to improve the four-fin ICS-SWH performance by optimising the fin spacing. Prior to simulation, issues regarding the parameters influencing fin optimisation need to be determined, constraints stated, heat transfer parameters outlined, and the type of CFD analysis established.

Fin material, length, thickness, and the number of fins in the ICS-SWH are the four main parameters to be defined when analysing fin optimisation. The material thermal conductivity is an intrinsic parameter for an effective ICS-SWH. The low density, high thermal conductivity and recyclable properties of aluminium highlighted the suitability of this material as already discussed in section 3.1.1.

The fin length was fixed at a maximum of 800mm. Fins are used to increase the heat transfer from the heated surface by increasing the effective surface area. The effectiveness of the fin is enhanced by increasing the ratio of the perimeter to the cross-sectional area () as stated by Incropera and Dewitt (2001) therefore the use of thin, but closely spaced fins is preferred, with the provision that the fin gap is not reduced to a value where flow between the fins is severely impeded, thereby reducing the convection coefficient. The study investigated the improvement in performance of the ICS-SWH by increasing the number of fins.

Three main constraints were taken into consideration for design improvement and included: cost, volume (50 litre tank size) and manufacturing ability.

Three main heat transfer parameters influence the ICS-SWH performance and can be recapitulated as: the shape of fins, the angle of inclination of the heater, and time of exposure to incident solar radiation. Due to manufacturing constraints, simple rectangular shapes of fins were considered. A 45° inclination angle and a 300W/m2 heat flux were taken as the reference conditions.

Finally, the type of CFD analysis, 2D or 3D, is an important parameter to consider. A previous study of Muneer et al (2006a) outlined that 2D analysis was sufficient for a satisfactory analysis of the system. However, 2D analysis would only suffice for a horizontal inclination of the heater. For any angle above zero a gradient exists in the longitudinal direction making a 2D analysis insufficient. Hence, based on a 45° inclination of the collector, a 3D analysis was undertaken. As the quiescent fluid is unavailable in CFD simulation, the process was assumed transient.

### Capabilities and limitations

CFD in simple terms is the use of computer and numerical methods to solve and analyse problems involving fluid flow. It is very often used in product concept, product development and also virtual prototyping as it provides complementary information about environmental performances and significantly reduces the amount of experimental work needed. CFD-Fluent software, based on the finite volume method offering a wide array of physical 2D and 3D models, was used for this study. Recent studies indicate an increase in the use of CFD tools for analysing and optimising design and performances of solar collector’s. This is despite some inaccurate predictions due to the assumptions involved in modelling calculations stated by Groenhout et al (2002). This model provided information about collector performance and was a useful tool for design improvements providing detailed pictures of fluid movements and stratification occurring in the collector.

Despite these advantages the CFD micro-model requires considerable skill to operate thus requiring an extended training time and incurs high annual license and maintenance costs. Regardless of an increased speed of computation available, CFD still cannot be used for real time computation. Numerical analyses require considerable time to set up and perform. Finally, software codes are locked which make them unavailable for improvements

### Model calibration

The modelling process was carried out for 3D analysis using CFD-Fluent 6.2 software. Gambit 2.2 was used to mesh the model. The simple and regular geometry of the model suggested the use of a quad structured mesh of size 1mm based on Henderson et al (2007). Two different boundary condition types were applied on the absorber plate for tests, depending on the purpose of the simulation. Optimisation simulations used a constant heat flux of 300W/m2 as the boundary condition on the absorber plate. A constant absorber plate temperature boundary condition was applied when comparing the heat absorbed by the two ICS-SWH designs. According to these conditions the program calculated the temperature field in the geometry and as a result values at the nodes were displayed. Results are presented in section 4.2.4.

### Modelling results

Stratification is essential for good performance of a solar collector and is significant when trying to optimise the collector for draw-off as was observed in Chapter 3; however, better mixing in the tank results in higher rates of heat transfer. Furthermore, the addition of fins might give a differential of temperature – lower from the top to the bottom of the ICS-SHW – but will optimise the transfer of energy into water. A CFD stratification analysis was developed for the four-fin ICS-SWH design and then undertaken for a second design using five fins to compare both water stratification and velocity magnitude for a given time and heat transfer through time.

#### Fin heat transfer

A good understanding of the influence of extended surfaces is important when seeking performance enhancement of the ICS-SWH. Figure 4-25 represents the temperature of the fins after an elapsed time of 60 minutes and a simulated heat flux on the absorber plate of 300 W/m2. Heat is transferred through the fins from the top of the collector to the bottom where the water temperature is cooler. This results from gravity and buoyancy effects. Water with different temperatures will settle at a height in the ICS-SWH corresponding to the density of the fluid. Hot water of low density will naturally settle in upper layers while cold water of high density will fall to the bottom layers. During the first three hours of the charging process, high temperature stratification occurs in the ICS-SWH.  With time, temperatures in the upper layers become fully established and reach an equilibrium causing the lower layer to increase in temperature and therefore decrease the density gradient of water inside the ICS-SWH.

Fig. 4-25: Temperature stratification of fins and middle line of water collector

In order to ease the comprehension of the analysis process a discussion of the initial four-fin collector design is discussed below.

#### Four-fin collector design

The display of the water velocity profile was completed in Figure 4-26. Velocity was observed to increase with the longitudinal length and then decrease as it gets closer to the top of the collector. This can be explained by the accumulation of hot water at the top of the collector reducing the velocity boundary layer and promoting diffusion of heat with time. It is observed in Figure 4-26 that an increase, followed by a decrease, pursued by an increase in velocity occurs between the fins. This decline in velocity between the fins suggests that additional fins could be incorporated in the design to increase the velocity magnitude.

Fig. 4-26: Velocity profile – 4 fins, top view, after 20 min

The horizontal plane view of velocity profile in Figure 4-27 supports this observation and shows that high velocities occur at the absorber plate where higher temperatures are experienced.

Fig. 4-27: Velocity profile – 4 fins, side view, after 20 min

Results showed that the overall velocity increased with time until it reached a peak value from which velocity magnitude declines with the passage of time. The increase is due to a high heat flux through the fins to the water occurring after the initial capacitance effect of the system. With time, hot water builds up at the top of the collector as shown in Figure 4-28 resulting in a decline of heat transfer and therefore heat is diffused from the system.

Fig. 4-28: Longitudinal water temperature stratification – 4 fins, front view, after 20min

Figures 4-28 and 4-29 represent the longitudinal temperature stratification in the collector inclined at 45(. As predicted, higher temperatures occur in the top of the collector. Stratification occurs for a maximum water temperature of 295.9(K at the top of the collector to a minimum temperature of 293.3(K at the bottom; a 2.6(K temperature gradient.

Fig. 4-29: Longitudinal water temperature stratification – 4 fins, side view, after 20min

In an attempt to improve the heat transfer one fin was added to the original ICS-SWH design. New 3D velocity and stratification analysis were undertaken for the five-fin ICS-SWH configuration.

#### Five-fin collector design

Figures 4-30 and 4-31 display the velocity profile of the new ICS-SWH. An increase in velocity, compared to the four-fin design was observed resulting in an increase of 2% in the maximum velocity. The main velocity pattern occurs between 1.90mm/s to 3.8mm/s for the five-fin collector compared with a 1.86mm/s to 3.72mm/s for four-fin design.

Fig. 4-30: Velocity profile – 5 fins, top view, after 20 min

Fig. 4-31: Velocity profile – 5 fins, side view, after 20 min

The longitudinal temperature stratification of the five fin collector is shown in Figure 4-32. Stratification occurs from a maximum water temperature of 295.9(K at the top to a minimum temperature of 293.8(K at the bottom of the collector, resulting in a 2.1(K temperature difference. This corresponds to a 19% decrease in stratification.

Fig. 4-32: Longitudinal water temperature stratification - 5 fins, side view, after 20min

#### Improvements

Previous observation showed that the five-fin collector achieved an increase in velocity of 2% compared to the four-fin design, while longitudinal water temperature stratification decreased by 19%. This could be explained by the addition of the fins responsible for an increased transfer of heat inside the collector, thus increasing velocity and overall temperature in the collector.

In order to demonstrate that five fins is a more suitable geometry arrangement for optimal collector design, a 3D CFD analysis was carried out assuming a constant temperature boundary condition on the absorber plate set at 313(K. The fluid departure temperature was set at 293K. Despite the fact that the system is under a constant heat flux, using a constant input temperature allowed the heat absorbed by both collectors to be derived as shown in Figure 4-33.

Fig. 4-33: Heat transfer and water temperature profiles in the ICS-SWH

Assuming a constant temperature boundary condition on the absorber plate resulted in high rates of heat transmittance. This figure allows a comparison of the rate heat is absorbed by both collectors. Initially, for the first ten minutes, more heat was absorbed by the five-fin collector compared to the four-fin. This is linked to a frenzy of heat transfer activity as the fins are surrounded by cooler water. After ten minutes the five fins are surrounded with warmer water than the four fin design. The difference in temperature between the four fins and the water is higher resulting in a higher heat flux. Both profiles reach a peak value at the equilibrium temperature 313(K set as the boundary condition.

### Discussion on CFD

This section reported the implementation of a four-fin ICS-SWH concept utilising CFD-Fluent software through Gambit in order to optimise its design performance. Initial results of the four-fin ICS-SWH indicated that one fin could be added to the original design to improve the heat transfer. A 3D CFD simulation was then undertaken for a five-fin ICS-SWH. Two boundary conditions were applied to the systems in order to compare the water temperature stratification achieved and the heat transferred to the water body by each collector.

The first boundary condition applied to the systems consisted of a constant heat flux on the absorber plate. This method was used to characterise the temperature stratification and the velocity magnitude within both collectors. Despite a minor decrease in temperature gradient between the top to bottom in the five-fin ICS-SWH, it was clearly observed that stratification remained. It is important to state that the addition of fins should not impede the flow between the fins (as was experienced when trialling a multi-fin design in an earlier study), thereby reducing the convection coefficient as stated by Incropera and Dewitt (2001). Results showed that the addition of one fin in the collector increased the velocity in the collector which has a corresponding increase on the Nusselt number; raising the heat transfer coefficient in a predictable manner as stated by Ozoe (1974a). The velocity magnitude was also observed to decrease with time for both collectors with the water becoming warmer.

A second boundary condition applied to the systems consisted of a constant temperature on the absorber plate which was used to characterise the heat absorbed by each collector. Results revealed that the addition of one fin accounts for the increased transfer of heat inside the collector. It was observed that the five fins supplied more energy to the collector than four at the beginning of the charging process. The intermittent availability of incident solar radiation in Scotland shows high potential for this type of improvement as it is advantageous to have a rapid heating process.

In light of the results presented in this paper, the five-fin collector performed generally better than the original four-fin collector. Therefore, this new design could be suggested as a new arrangement of the collector assuming that the cost associated with this improvement is negligible.

## Concluding remarks

This chapter explored the modelling of ICS-SWH’s in order to assess their performance. To start with, two macro-models for fluid flow and heat transfer were developed using Visual Basic for Applications (VBA). Both generated corresponding bulk water temperature’s in the collector with given hourly incident solar radiation (W/m2), ambient temperature and inlet water temperature and therefore predictable ICS-SWH performances. The first model was developed for laboratory conditions and modelled bulk water temperature and stratification profiles over time in an ICS-SWH while the second model predicted the bulk water temperature in the ICS-SWH for field weather conditions.

Statistical methods and extreme range tests suggested that both models were robust and could predict the performance of an ICS-SWH at any location and with different installation configurations. The field macro-model also demonstrated that a simulation could be extended which could result in a useful tool to estimate the perennial performance of the ICS-SWH. A life cycle assessment (LCA) based on this statement was then carried out and is presented in Chapter 5. An account of uncertainties and propagation of errors associated with modelling and the accuracy of statistical methods used was addressed.

A CFD-Fluent analysis of the four-fin ICS-SWH concept was simulated in order to optimise the design performance of the original concept and resulted in a new simulation for a five-fin ICS-SWH. The new design showed high potential for Scottish applications due to its rapid heating process which is advantageous in locations where availability of incident solar radiation is intermittent. Therefore, this design could be suggested as a new arrangement of the collector assuming that the cost associated with this improvement is negligible.

In conclusion, this section of the thesis opens an avenue for future ICS-SWH design optimisation but also widens the utilisation of the field macro-model developed by showing its potential to provide data for a full year’s performance and therefore provide an effective life cycle assessment of the ICS-SWH.

Fig. 4-34: Total data - measured and computed for a 50 day period: 7th June – 27th July 2007

# LIFE CYCLE ASSESSMENT (LCA)

Industries apply Life Cycle Assessment (LCA) as a technique to identify significant environmental impacts of their products in order to improve their environmental performance during their whole life cycle. This chapter performs a streamlined LCA of different types of ICS-SWH designed for use in a Scottish environment. Firstly, the goal and scope of the LCA were described. A material inventory providing general information regarding material production processes used in the ICS-SWHs was provided. An energy analysis of the ICS-SWHs using embodied energy of materials, complemented by their associated environmental impacts were then dealt with. Finally, a monetary analysis (MA) was provided enabling a cost comparison of the different ICS-SWH alternatives identifying their value per pound Sterling spent.

## Goal and Scope

The first step is to define the reference metric used in this study to quantify performance of the ICS-SWH. International Organization for Standardization - ISO (2006) demonstrates that a reference unit in any LCA needs to be determined in order to compare collected data from different studies of the same product category. This study is carried out to determine the best ICS-SWH alternative between three ICS-SWHs presented for analysis. Based on the work of Ardente et al (2003), a reference unit (or Functional Unit) equal to the entire equipment was used to benchmark this analysis.

The three ICS-SWHs systems assessed in this study correspond to two aluminium construction of 1.5 and 3mm thickness (AL-1.5 and AL-3) and one of stainless-steel of 1.5mm (ST-1.5) incorporating extended heat transfer surfaces. Each ICS-SWH is composed of three main components identified below and shown in Figure 5-1:

- The collector (including the absorber plate and the water tank)

- The glass wool insulation

- The glass cover

- The wooden box

Fig. 5-1: Sectional view of the aluminium ICS SWH. Note: a dimension drawing is shown in Figure 3-1

The collector was categorised as a passive ICS-SWH. The water tank and absorber plate are integrated into one unit. This type of collector is recommended for medium to low temperature domestic water heating applications. The ICS-SWHs were assumed to be directly installed on sloping roofs of 45( angle of inclination. Impacts associated with each collector component were analysed in order to identify the main life cycle issues affecting each component of the ICS-SWHs.

The LCA of each ICS-SWH type will provide an analysis of the environmental benefit of operating these heaters in Scottish weather conditions in order to appreciate if this tool can identify a best ICS-SWHs alternative. A material inventory introducing the main component production processes was first carried out to understand their potential harms to the environment and their energy requirements during production. An energy and environmental impact analysis for each component was then performed. Interpretation of results by introducing energy savings and carbon emission reduction followed by a monetary saving analysis were determined. Assumptions for the analysis included a typical water inlet temperature of 12(C for Scotland and a domestic hot water (DHW) demand temperature of 55(C, assuming a daily draw-off regime of water at 4pm. On days of poor insolation either electric or hydrocarbon back-up sources elevate the water temperature to 55°C, this is accounted in the LCA and cost analysis. The DTI (2002) stated that the average population of a UK home is approximately three people, with each consuming 50 litres of hot water per day as identified in a later survey carried on behalf of DTI (2005) and DEFRA. Given that the capacity of the ICS-SWHs is 50 litres with 1m2 of collector plate, all interpretations were based on the installation of 3m2 of collector plate or 150 litres to meet typical domestic demand from an installation.

## Material inventory

The following section discusses the processes involved in production of the main materials used in the construction of the ICS-SWHs.

### Stainless-steel

There are a number of stages involved in producing stainless-steel for commercial use. Stainless-steel is produced from ore and scrap metal. The principal ore used is hematite which contains almost 70% iron. Scrap iron and stainless-steel and various alloys of chromium (and nickel, molybdenum etc. depending on the stainless type) are used in stainless-steel making today. The main process used at present for refining stainless-steel is the electric arc furnace used to produce carbon and alloy steels. A current is passed through an electrode resulting in a temperature increase to a point where the scrap and alloys melt. The molten material is then transferred into an Argon Oxygen Decarbonisation container, where the carbon levels are reduced and the final alloy additions are made to make the composition chemistry depending on the type of stainless-steel.

Stainless-steels are a group of high alloy steels that are designed to provide high corrosion resistance. This is provided by the thin oxide film which forms due to the chromium element in the stainless-steel reacting with oxygen in the atmosphere. The stainless-steel 304 used in this study is classified as an austenitic steel with an alloy containing 18-20% of chromium and 8-10% of nickel resulting in a very ductile material and a good corrosion resistance as stated by Groover (2006).

### Aluminium

In a similar fashion, aluminium is produced from ore (Bauxite) and scrap metal. Bauxite is mined and refined in order to extract aluminium for use. The ore is first washed and crushed into a fine powder. The aluminium is then extracted from the bauxite as aluminium oxide (alumina) which is subsequently broken down and separated into aluminium and oxygen gas using an electrolysis process also called smelting. The aluminium is then alloyed with other materials and is then processed through casting, rolling or extrusion for further fabrication of aluminium products.

Aluminium is one of the newer materials among the principal metals on the market. Its low density made it an attractive choice use in engineering. Aluminium also has high electrical and thermal conductivity and an excellent corrosion resistance due to the thin layer of aluminium oxide that forms on its surface when exposed to oxygen. It is a very ductile material and although it is known to be relatively low in strength it can be alloyed and heat treated to allow it to compete with steels.

### Glass wool insulation

Glass-wool is produced from raw materials such as sand, recycled glass, soda ash, limestone and glass-wool scrap from the production process. Reusing of waste off-cuts into the production process reduces raw material input and therefore energy requirements.

Recycled glass from building windows, car glass and bottle glass is increasingly used in the manufacturing of glass wool accounting for 30% to 60% of the raw material input. The raw material mix is then melted at high temperature ranging from 1300°C to 1500°C in an electric or gas furnace while fumes and dusts are cleaned by filters to minimise environmental impact.

The melted glass is then converted into fibres with its passage through a spinner drilled with holes and through a fibre attenuation using high temperature gas jet streams. Small quantities of binding agents are then added to the fibres in order to give the desired structure and density required for its end-use application. The glass wool mat finally goes to a curing oven heated at around 200°C where it gets its final shape, strength and stability, and where it is laminated and polymerised. The glass wool is then cut in width and length at the required dimensions according to its final usage. The product is then tightly compressed in order to reduce the product volume in the packaging resulting in an easier and cheaper storage and transport of the product. Figure 5-2 represents the glass wool production process illustrated by the European Insulation Manufacturers Association - ERIMA (2007).

Fig. 5-2: Glass wool production process, Source: ERIMA (2007)

### Window glass

The window glass is produced using the float glass method. Raw materials such as soda lime glass which principally contains silica sand, soda ash and limestone are mixed and weighed and then flow into a furnace heated to 1500°C. Melting, refining and homogenising take place simultaneously in the furnace and determine the glass quality. Compositions of the glass can be modified during this process to change the properties of the finished product such as adding magnesia to help reduce devitrification as stated by Groover (2006).

The molten glass is then fed onto a float bath where it is floated on top of a bath of molten tin in a continuous ribbon and starts to cool slowly. The ribbon then goes through a coating stage through chemical vapour deposition laying down a variety of coatings to vary the optical properties of float glass depending on the final application. The ribbon then passes through an annealing process where glass is slowly cooled in a Lehr oven to prevent build up of stress. The glass is cooled under controlled conditions until it reaches room temperature and is then cut to the desired shape and size. Figure 5-3 represents the window glass production process illustrated by Made How (2007).

Fig. 5-3: Window glasss production process, Source: Made How (2007)

### Timber

The timber frame was produced from UK grown mixed conifer logs through a sawmill process. In the first stage the grading process pre-sorts conifer logs into size and end use, before input to the sawmill. The logs then go through a debarker prior to sawing to remove bark from logs. The bark waste is then reused as raw material for horticulture. Subsequently debarked logs go through the sawmill to produce dimensional lumber. The cut products are then sorted through infra-red scanning equipment ensuring that only product of the required grade is included in the finished pack. The timber is then cut to the desired lengths by multiple cross cut machinery for the packaging process. Finally, preservative treatment is applied to timber products to ensure long term protection and service life of the timber.

## Energy analysis

The energy analysis concerns energy flows occurring during the life cycle of the product. The energy consumption can be split in two phases: Direct energy and Embodied energy.  Direct energy corresponds to the energy used during a life cycle step including electricity or heat energy employed during the production of the collector or fuel for transport. Embodied energy corresponds to the energy consumed by all the processes associated with the production of the individual materials employed.

The total energy consumption is obtained by summing embodied and direct energy contributions. However, Ardente et al (2005a) showed that direct energy consumption only account for 10% of the overall energy consumption. Therefore, the streamlined LCA only accounts for embodied energy involved in the production processes of the ICS-SWHs materials.

Embodied energy assesses the total primary energy consumed over the whole life time of a product with the boundaries ideally being set from the extraction of raw materials to the end of the product’s lifetime; a boundary condition which is known as “cradle to grave”. Data regarding the embodied energy of materials refers to the Inventory of Carbon and Energy report issued by Hammond and Jones (2006). Embodied energy of each material presented in Table 5-1 is based on average UK market data.

Table 5-1: Embodied energy of materials

| Material | Embodied energy (MJ/kg) |
| --- | --- |
| Stainless-steel | 51.5 |
| Aluminium | 150.2 |
| Glass | 13.5 |
| Timber | 8.7 |
| Glass wool | 28.0 |

The aluminium embodied energy production was found to be 150.2 MJ/kg corresponding to an average of 33% recycled and 67% raw aluminium material. Future scenarios could be imagined of 85% recycled and 15% raw aluminium material which would reduce the embodied energy of aluminium production process to 53.7J/kg.

A breakdown of the materials used to produce the final ICS-SWHs was quantified in order to calculate their respective overall embodied energy. Table 5-2 reports the mass balance of a 1m2 collector summarising the quantity of materials required for each ICS-SWH.

Table 5-2: Mass balance of the collectors

| Collector type | Material | Mass (kg) |
| --- | --- | --- |
| Stainless-steel | Stainless-steel (1.5mm sheet) | 28.0 |
| 1.5mm | Glass | 12.6 |
|  | Timber | 30.7 |
|  | Glass wool | 3.5 |
| Aluminium | Aluminium (1.5mm sheet) | 9.8 |
| 1.5mm | Glass | 12.6 |
|  | Timber | 30.7 |
|  | Glass wool | 3.5 |
| Aluminium | Aluminium (3mm sheet) | 19.6 |
| 3mm | Glass | 12.6 |
|  | Timber | 30.7 |
|  | Glass wool | 3.5 |

The embodied energy and effect on the energy balance of materials involved in the construction of the ICS-SWHs were then calculated; hence the overall embodied energy of the ICS-SWHs was determined. Table 5-3 provides information gathered on each ICS-SWH.

Table 5-3: Embodied energy and incidence of materials on the energy balance

| Collector type | Material | Embodied energy (MJ) | Incidence (%) |
| --- | --- | --- | --- |
| Stainless-steel | Stainless-steel (1.5mm sheet) | 1442.0 | 73.0 |
| 1.5mm | Timber | 265.7 | 13.5 |
|  | Glass | 169.7 | 8.6 |
|  | Glass wool | 97.2 | 4.9 |
|  | Total | 1974.6 | 100.0 |
| Aluminium | Aluminium (1.5mm sheet) | 1472.0 | 73.4 |
| 1.5mm | Timber | 265.7 | 13.3 |
|  | Glass | 169.7 | 8.5 |
|  | Glass wool | 97.2 | 4.8 |
|  | Total | 2004.6 | 100.0 |
| Aluminium | Aluminium (3mm sheet) | 2943.9 | 84.7 |
| 3mm | Timber | 265.7 | 7.6 |
|  | Glass | 169.7 | 4.9 |
|  | Glass wool | 97.2 | 2.8 |
|  | Total | 3476.5 | 100.0 |

Based on the earlier discussed DTI (2002) study in section 5.1, results have to be translated to 3m2 of collector plate or 150 litres, to reproduce an appropriate study for UK homes. Primary energy consumption, measured in kWh, for the production of 3m2 ICS-SWHs during the complete life cycle phase, , is represented in Table 5-4.

Table 5-4: Energy analysis for a 3m2 installation

| Collector type | Material | Embodied energy (kWh) |
| --- | --- | --- |
| Stainless-steel 1.5mm | Stainless-steel (1.5mm sheet) | 1645.5 |
| Aluminium 1.5mm | Aluminium (1.5mm sheet) | 1670.4 |
| Aluminium 3mm | Aluminium (3mm sheet) | 2897.1 |

The energy analysis provided the total energy and material consumption for the production of each ICS-SWH. This analysis enables the evaluation of comparative environmental impacts and potential improvements which are provided in the following sections.

## Environmental impacts

This section aims to provide an understanding and evaluation of the magnitude and significance of the potential environmental impacts of each ICS-SWH. Resource consumption, air emissions, water emissions, waste and solid pollutants are the main environmental impacts. However, the streamlined LCA only accounted for the environmental impact of air emissions in order to ease the system analysis.

This environmental impact can be classified as either a direct or indirect emission. Based on Ardente et al’s (2005a) study, direct emissions were neglected as they generally represent an overall incidence of 10%. Therefore, only indirect emissions were considered. Indirect emissions are mainly related to the raw materials production process.

Based on the IPCC (2007) report, increased industrial activity and other human activities have increased CO2 concentrations in the atmosphere. CO2 being a greenhouse gas, this could result in an increase in mean global temperature. Based on this statement CO2 was chosen as the indicator of this category and embodied CO2 associated with the raw material production process of each ICS-SWHs was determined. Embodied CO2 refers to the amount of carbon dioxide emissions that result from the processes required to produce the finished product. Data regarding the embodied carbon of materials refers to the Inventory of Carbon and Energy report issued by Hammond and Jones (2006). Embodied CO2 emissions of each material are presented in Table 5-4 and refer to UK average market data.

Table 5-5: Embodied carbon dioxide of materials

| Material | Embodied CO2 (kgCO2/kg) |
| --- | --- |
| Stainless-steel | 6.2 |
| Virgin aluminium | 8.4 |
| Glass | 0.8 |
| Timber | 0.5 |
| Glass wool | 1.4 |

The embodied carbon UK average data of aluminium production was found to be 8.35 kgCO2/kg. Future scenarios having 85% recycled and 15% raw aluminium material would bring the embodied carbon down to 3.17 kgCO2/kg.

Based on the figures from Table 5-2 the embodied carbon and effect on the energy balance of materials involved in construction of the ICS-SWHs was then calculated; hence the overall embodied carbon of the ICS-SWHs was determined. Table 5-5 provides information gathered on each collector.

Table 5-6: Embodied energy and impacts of materials on the energy balance

| Collector type | Material | Embodied CO2 (kgCO2) | Impacts (%) |
| --- | --- | --- | --- |
| Stainless-steel | Stainless-steel | 172.2 | 85.6 |
| 1.5mm | Timber | 14.6 | 7.3 |
|  | Glass | 9.7 | 4.8 |
|  | Glass wool | 4.7 | 2.3 |
|  | Total | 201.2 | 100 |
| Aluminium | Aluminium | 81.8 | 73.8 |
| 1.5mm | Timber | 14.6 | 13.2 |
|  | Glass | 9.7 | 8.8 |
|  | Glass wool | 4.7 | 4.2 |
|  | Total | 110.8 | 100 |
| Aluminium | Aluminium | 163.7 | 85.0 |
| 3mm | Timber | 14.6 | 7.6 |
|  | Glass | 9.7 | 5.0 |
|  | Glass wool | 4.7 | 2.4 |
|  | Total | 192.7 | 100 |

Based on the DTI (2002) study the environmental impacts were considered for 3m2 of collector plate or 150 litres. Total CO2 emissions, , related to the production of 3m2 ICS-SWHs are represented in Table 5-7.

Table 5-7: Total CO2 emissions for a 3m2 installation

| Collector type | Material | Embodied CO2 (kgCO2) |
| --- | --- | --- |
| Stainless-steel 1.5mm | Stainless-steel (1.5mm sheet) | 603.6 |
| Aluminium 1.5mm | Aluminium (1.5mm sheet) | 332.4 |
| Aluminium 3mm | Aluminium (3mm sheet) | 577.9 |

## Interpretation

### Identification of Energy and Environmental issues

An analysis of the energy and environmental impacts developed in sections 5.3 and 5.4 was performed in order to identify and evaluate the significant issues based on the above results. It is a valuable step in order to compare the different production alternatives and which material input has the most impact on ICS-SWH construction.

      - Energy issues

The embodied energy related to the collector production depends on the material type and mass and is the main contributor to the ICS-SWHs overall embodied energy. The embodied energy associated with each material depends on the quantity needed and the energy intensity of the material’s production.

Although the embodied energy per kilogram of aluminium is 66% higher than stainless-steel, the overall embodied energy of the collector, for an identical material thickness, is of the same magnitude as shown in Table 5-3. This is explained by the 65% lower aluminium density of 2770kg/m3 compared with 7900kg/m3 for stainless-steel.

It was also observed from Table 5-1 and 5-3 that from the three remaining materials (glass, timber and glass-wool), glass wool has the highest embodied energy per kilogram but has the smallest effect on the overall ICS-SWH embodied energy due to its low mass. Vice versa the overall embodied energy of timber was found much higher than glass-wool. This is explained by the timber mass being nine times that of glass-wool. Similar observations were made for the glass compared with timber and glass-wool materials.

      - Environmental issues

The embodied carbon emissions associated with each material depends on the CO2 released during their production; depending essentially on the type of fossil fuels used and the amount of material needed.

Although the embodied carbon emissions per kilogram of aluminium are 26% higher than the stainless-steel; as shown in Table 5-5, the overall embodied carbon emissions of each collector, for an identical material thickness, is 45% lower by using aluminium as shown in Table 5-6. It was also noted that even by doubling the thickness of the aluminium (AL-3), the embodied carbon emissions are still 4% lower than the ST-1.5. This can be explained by the recyclable property of aluminium. This verifies the statement made in the above section 5.5.1.1, showing that despite the higher embodied carbon emissions per kilogram of aluminium, the lower mass of aluminium needed to produce an identical collector resulted in lower overall embodied carbon emissions.

Each material was then weighed to calculate their contribution to the overall carbon emissions of each ICS-SWH. Again, it was observed from Table 5-5 and 5-6 that from the three remaining materials (glass, timber and glass-wool), glass wool had the highest embodied carbon emissions per kilogram but resulted in the smallest effect on the overall ICS-SWH embodied carbon emissions due to its low mass. Vice versa timber had the lowest embodied carbon emissions per kilogram despite having the biggest effect on the overall ICS-SWH embodied carbon emissions due to its higher mass.

### ICS-SWHs energy and carbon dioxide savings

A cost-benefit analysis of the energy and environmental parameters of each ICS-SWH was performed in this section. For this analysis the useful energy saved annually, , and CO2 emission savings,, need to be determined.

      - System output

The macro-model developed in Chapter 4 for field weather conditions was used to generate corresponding bulk water temperature in the collector for each ICS-SWH. Data regarding the hourly solar radiation and other climatic parameters necessary for the simulation come from the European Commission Joint Research Centre, Institute for Environment and Sustainability (IES) (2007) for Edinburgh location. The daily, monthly and annual energy savings and CO2 emission savings were then determined assuming a typical inlet water temperature of 12(C for Scotland and a required temperature of 55(C supposing a draw-off of water at 4pm daily.

The daily potential energy outputs from using the ICS-SWHs were calculated using equation 5.1.

(5.1)

Where 	 	is the inlet/outlet temperature difference of the water ((C)

is the assumed inlet temperature of the water of 12(C ((C)

is the modelled output water temperature at 4pm ((C)

is the daily water flow rate assumed at 150l/day for 3m2 collector area

is the specific heat capacity of the water (J/kg.(C)

The variation of the specific heat capacity of water over this temperature range is negligible with a maximum variation of about 0.4% and was therefore assumed constant at 4.2kJ/kg.(C.

Monthly and useful energy saved annually, , were then calculated for each ICS-SWH. Figure 5-4 presents useful energy saved annually by each ICS-SWH. This figure was based on a 3m2 collector area installation heating 150 litres of water per day from a starting temperature of 12°C to the required temperature of 55°C in Edinburgh weather conditions.

Fig. 5-4: Useful energy saved annually for each ICS-SWH

The annual energy saving from using AL-3, AL-1.5 and ST-1.5 ICS-SWHs were found to be 1109kWh, 1107kWh, 1041kWh respectively. Based on the previous assumption, 2747kWh is annually required to raise the daily 150 litres of water from 12°C to 55°C. The ICS-SWHs did not raise the water by the required amount but partially fulfil the daily domestic hot water needs. AL-3, AL-1.5 and ST-1.5 ICS-SWHs could save up to 40.4%, 40.3% and 37.9% of the required energy. Using a more conductive material resulted in a 2.4% annual increase of energy savings while increasing the material thickness resulted in only 0.1% annual increase.

A detailed picture of the monthly energy coverage (EC) of each ICS-SWH is provided in Figure 5-5. The energy coverage represents the percentage ratio of the energy saved and energy required to raise the 150 litres of water from 12°C to 55°C.

Fig. 5-5: Solar fraction of AL-3, AL-1.5 and ST-1.5. Note: solar fraction is the amount of energy provided by the ICS-SWH divided by the energy required to raise water temperature to 55oC

For each month it is evident that the ST-1.5 is under-performing compared with aluminium ICS-SWHs. The AL-1.5 is slightly out-performed by the AL-3 ICS-SWH, however AL-1.5 uses half the amount of material therefore suggesting AL-1.5 as the best alternative. Each annual energy saving has an associated annual CO2 emission saving presented in the next section.

      - CO2 savings

Domestic water heating is primarily accomplished using natural gas or electricity with natural gas accounting for 60% of the UK water heating systems. In order to quantify the annual CO2 emission savings, , detailed fuel conversion factors were introduced. Such factors provide CO2 emissions expressed per unit activity such as fuel or electricity consumed or distance travelled. Electricity and natural gas conversion factors represents the fuel mix used for electricity generation, quality of coal consumed, composition of the vehicle fleet and journey taken in that year. Based on data from the UK inventory of Greenhouse Gas emissions produced for Department for Environment, Food and Rural Affairs – DEFRA (2005), electricity and natural gas conversion factors were taken as 0.43kgCO2/kWh and 0.19kgCO2/kWh respectively. The annual CO2 emission savings of each ICS-SWHs were then calculated depending on the fuel used in the household and are presented in Figure 5-6.

Fig. 5-6: Annual CO2 savings by fuel type using ICS-SWHs

Depending on the type of ICS-SWH installed there is a potential for saving of 198-211 kgCO2 per year if assisting a gas water heating system. While this may seem an insignificant figure in terms of the overall targets set under the Kyoto protocol, if half of the 25 million homes in the UK had an ICS-SWH system installed to assist their daily hot water needs, around 2.6 MtCO2 per year could be saved.

These results show that installation of ICS-SWHs in UK homes can contribute to significant carbon dioxide reduction. In order to determine which of the three ICS-SWHs would be the most viable solution, an energy payback time (EPBT) and carbon dioxide emission payback time (ECPBT) were carried out in the next sections.

### Energy payback time – EPBT

The energy payback time (EPBT) is defined by Ardente et al (2005b) as the time necessary for an ICS-SWH to collect the energy equivalent to that used to produce it. Therefore the EPBT can be expressed in equation 5.2.

(5.2)

Where 	 is the energy input during the ICS-SWH life cycle (kWh),  is the annual useful energy saved by using the ICS-SWH (kWh/year) and  is the annual energy employed during the use of the ICS-SWH (kWh/year).

The use of a passive collector system or a solar driven pump was therefore assumed for  to be null. Hence EPBT were calculated for AL-3, AL-1.5 and ST-1.5. Results are presented in Table 5-8.

Table 5-8: EPBT

| Collector type | (kWh) | (kWh/year) | EPBT (years) |
| --- | --- | --- | --- |
| ST-1.5 | 1646 | 1041 | 1.6 |
| AL-1.5 | 1670 | 1107 | 1.5 |
| AL-3 | 2897 | 1109 | 2.6 |

The energy payback times related to the studied ICS-SWHs were found to be lower than three years. This value shows the great energy potential of such technology. A common thought would be that the aluminium payback period should be significantly longer because of its more intensive production process resulting in embodied energy value per kilogram of material being three times the stainless-steel one. However, the recycling property of aluminium decreases its embodied energy, bringing down the energy payback time considerably. Future scenario of 85% recycled and 15% raw aluminium material would lower the embodied energy of aluminium production therefore reducing the EPBT of AL-1.5 to 10 months.

### Carbon dioxide emission payback time – ECPBT

The ECPBT was calculated based on the previously calculated annual emission savings of CO2, , in section 5.5.2.2. The ECPBT can be defined as the time necessary for an ICS-SWH to equal the CO2 emissions released during the production and use of the installation itself as stated by Ardente et al (2005b). It summarises the total impacts during the life cycle and the emission savings. The ECPBT is expressed in equation 5.3.

(5.3)

Where  is the total CO2 emissions related to the production of a 3m2 ICS-SWH during its life cycle (kgCO2) represented in Table 5-7,  is the annual CO2 emission saving (kgCO2/year) represented in Figure 5-6 and  is the annual CO2 emissions related to the ICS-SWH use (kgCO2/year). represents the emissions saved by using the ICS-SWH compared to the auxiliary system used in the household to deliver hot water and therefore depends on the type of auxiliary heater employed.

The use of a passive collector system or a solar driven pump was assumed therefore  was set to null. ECPBT for AL-3, AL-1.5 and ST-1.5 were calculated and results are presented in Table 5-9 and Figure 5-7.

Table 5-9: ECPBT

| Collector type | (kgCO2) | (kgCO2/year) | ECPBT (years) |
| --- | --- | --- | --- |
|  |  | Gas | Electricity | Gas | Electricity |
| ST-1.5 | 604 | 198 | 448 | 3.1 | 1.3 |
| AL-1.5 | 332 | 210 | 476 | 1.6 | 0.7 |
| AL-3 | 578 | 211 | 477 | 2.7 | 1.2 |

Fig. 5-7: ICS-SWH ECPBT: Categorisation with respect to fuel type

The carbon dioxide payback period depends on the auxiliary system used by the household. Like the energy payback-time, the CO2 payback-time results were generally lower than three years.

The per unit CO2 evolution of electricity is much higher than natural gas resulting in shorter environmental payback period for households using electricity as an auxiliary heating system. This is due to electricity having a high environmental impact due to the fuel mix used in its generation. ECPBT ranges from 1.6, 2.7 to 3.1 years for the AL-1.5, AL-3 to ST-1.5 respectively using gas while using electricity would result in a decrease of ECPBT to 8 months, 1.2 and 1.3 years respectively; corresponding to a 56% difference in ECPBT depending on the fuel type.

A considerable variation in the payback time of collectors of identical dimensions, Al-1.5 and ST-1.5, was observed. This is explained by the recyclable property of aluminium diminishing its embodied carbon and by its higher thermal conductivity resulting in higher energy gain. A payback period based on future scenarios of 85% recycled and 15% raw aluminium material would result in lowering the ECPBT to 10 and 5 months when gas and electricity auxiliary heating systems are used.

### Conclusions and recommendations

An LCA was carried out for each ICS-SWH type in order to establish the ICS-SWH with the smallest carbon footprint. It was found that despite the high amount of energy to produce aluminium, the “light” and recyclable properties of the material resulted in similar embodied energy when compared with stainless-steel. This resulted in a smaller environmental impact due to lower carbon emissions released to the atmosphere during the production process.

Energy and carbon dioxide savings associated by using those ICS-SWHs were modelled and showed that although the AL-1.5 ICS-SWH was out-performed by 0.1% by the AL-3 ICS-SWH, the fact that it only uses half the amount of material in producion makes it more viable. The carbon dioxide savings showed that depending on the ICS-SWH installed there is a potential for saving 6% more kgCO2 per year by using an Al-1.5 compare with a ST-1.5 and only 0.5% by increasing the thickness of a same ICS-SWH material.

The EPBT of the ICS-SWHs was found to be consistently lower than three years for all ICS-SWHs with the lowest EPBT value of 1 year 7 months achieved by the AL-1.5 ICS-SWH. This value shows the great energy potential of such a ICS-SWH design. The calculations of the carbon dioxide emission payback times confirm the higher potential of using an AL-1.5 ICS-SWH by decreasing the ECPBT by 42% and 48% when compared with AL-3 and ST-1.5 ICS-SWHs respectively.

All results point to the AL-1.5 ICS-SWH as the best alternative to operate in Scottish weather conditions. It would therefore be recommended to use an AL-1.5 ICS-SWH for further investigations due to its energy and environmental benefits. Increasing the recyclable percentage in the AL-1.5 could significantly reduce the environmental impact of the collector. Copper and brass could be realistic alternatives to use in the manufacture of the ICS-SWH in terms of embodied energy, malleability and thermal conductivity. However, the cost of these materials being so much higher than that of stainless-steel or aluminium would not make them economically viable. Economics plays a central role in any decision to purchase a solar water heater system. The customer is unlikely to buy an ICS-SWH if they know that its only benefits are to the environment. Therefore, a monetary analysis was developed to consider the economics of each system to ensure that such ICS-SWHs will be profitable.

## Monetary analysis (MA)

The monetary analysis (MA) can be defined as an economic evaluation technique to determine the total cost of owning and operating a product with time. The value of a MA lies in the ability to compare the cost of product alternatives and to determine which one provides the best value per Sterling pound spent. In order to achieve an appropriate MA, an insight of the collector material costs is provided, followed by the actual cost of the ICS-SWHs and a monetary payback time (MPBT) assessment.

### Collector material costs

It is difficult to find a definite figure for the price of aluminium and stainless-steel as they commonly fluctuate. Average figures obtained for the last year from May 2007 to May 2008 would be £2900 per tonne of stainless-steel and £1445 per tonne of aluminium. The large price difference can have several possible explanations. The main factor of the cost difference between the two metals is the added cost of machining stainless-steel compared with aluminium; which is ductile and more easily machined. Wholesale metal suppliers MEPS and LME could guarantee costs up to three to four months but not further than that period which reflects the frequency with which prices vary. A comparison of the price trend of aluminium and stainless-steel over the last three years is shown in Figure 5-8.

Fig. 5-8: Cost comparison

Stainless-steel has been the more expensive of the two materials but both materials have been increasing at the same rate until recently. Over the course of the last three years the price of stainless-steel has risen beyond levels that anyone inside or outside the stainless-steel industry could have forecasted. There are a number of contributing factors that have lead to these increased costs.

1 - Chinese stainless-steel consumption

There has been a recent and important increase in Chinese consumption of stainless-steel which has caused a global price increase in spite of a consistent consumption for the rest of the world. China has experienced phenomenal growth in the last five years resulting in being the world’s largest stainless-steel consumer and has not yet reached its peak.

2 - Raw material shortage

Scrap metal comes from waste stainless-steel items. Moll (2006) announced a decline from 34.8% in 2004 to 32% by 2010 of the worldwide share of scrap in stainless-steel production suggesting that scrap is being consumed at a far greater rate than it is being created. This current scrap shortage results in a notable increase in scrap prices. Iron ore is another material which is currently in short supply due to the significant lack of investment in iron ore mines anywhere in the world except for China and South America. Another main reason is the shortage of nickel ore supply, a major raw material for stainless-steel production resulting in a high nickel price. These raw material shortages result in rising stainless-steel production costs.

2 - Stainless-steel production

According to the International Stainless-steel Forum - ISSF (2007) global stainless-steel production decreased by 2.9% in 2007. This happened across most regions and countries except for China and the Asian region accounting for 60% of the world's stainless-steel production. A strong increase in stainless-steel production occurred in the first half of 2007 followed by a collapsed in the second half of the year after nickel prices dropped resulting in stainless-steel being withdrawn from the first half of 2007 stocks.

3 - Shipping

Another item influencing stainless-steel prices is a shortage of shipping capacity. One of the factors behind the growth in international trade over the past decade is a reduced shipping cost but now the trade has grown to such an extent that there is a shortage of shipping available. The higher cost of shipping is hampering the movement of raw materials around the globe.

4 - Energy costs

Energy costs are another factor increasing stainless-steel production costs. Production cost increases due to higher energy input costs (i.e. Electricity is an output from many energy resources and is used to power most equipment and facilities). Energy markets are experiencing high demand and limited supplies, resulting in volatile market and high prices. Since energy is a key input in the production process, sharp increases per unit in goods occur as stated by Velazquez (2006). Stainless-steel being an energy intensive process uses significant energy input for their production resulting in higher costs.

### ICS-SWHs costs

The price of installing a domestic flat plate collector solar water heating system in the UK today is anywhere from £2,000 to £3,000 which would include delivery, installation and associated equipments costs as stated by EST (2007). The majority of solar water heating systems installed would come with a 5 to10 year warranty and require very little maintenance. The costs of the materials used in the ICS-SWHs investigated for this project are detailed in Table 5-10. Prices were updated to most recent material cost data collected in May 2008.

Table 5-10: Raw material costs per square meter of collector

| Collector type | Collector cost (£) | Material cost (£) | ICS-SWH cost (£) |
| --- | --- | --- | --- |
| Stainless-steel 1.5mm | 352 | 105 | 457 |
| Aluminium 1.5mm | 81 | 105 | 186 |
| Aluminium 3mm | 161 | 105 | 266 |

The difference in price of the two materials is a reflection of the recent surge in global stainless-steel prices. Aluminium prices were taken from London Metal Exchange (LME) while stainless-steel 304b prices were taken from MEPS International Ltd.  While the cost of materials may not be very high, the additional labour and delivery costs, along with other required parts such as a pump, controller, valves and piping would raise the price of parts up to the region of £1,000.

To encourage the public to become involved in the effort to reduce carbon emissions, government grants for homes that install these heating systems are made available. The UK government Low Carbon Buildings Programme (LCBP) offers a £400 grant for every professionally installed solar water heating system as stated by the DTI (2007). Another grant available in Scotland from the Scottish Community Householder Renewables Initiative (SCHRI) provides 30% of the installed cost up to a value of £4,000 as stated by the Energy Saving Trusts (2007).

### Monetary payback time (MPBT) analysis

The monetary payback time (MPBT) can be defined as the time necessary for the ICS-SWH to achieve the monetary equivalent to its capital cost and is expressed in equation 5.4.

(5.4)

is the capital cost associated with the ICS-SWH life cycle (£),   is the annual monetary saved by using the ICS-SWH (£/year) and  is the annual associated cost of using ICS-SWHs such as operational and maintenance costs (£/year).

Gull Industries (2008) also suggested that ICS-SWHs are virtually maintenance free although the glazing needs to be cleaned and the unit to be drained once a year, as is recommended for auxiliary water heaters. It was then assumed for this study that annual associated costs could be neglected, therefore setting   to null.

The potential annual monetary savings, , of a 3m2 ICS-SWHs installation vary considerably between homes using auxiliary gas fuelled or electric heating systems. The roller-coaster profile of energy prices in the UK will have a recognised impact on the study findings. Data of 12.1p/kWh for electricity and 3.6p/kWh including VAT for gas prices refers to domestic standard prices of Scottish Power and British Gas prices respectively in September 2008. Based on this reference prices, savings achieved by using each ICS-SWHs were calculated. Annual savings, , were calculated from equation 5.5.

(5.5)

Where  is the useful annual energy saved by using the ICS-SWH (kWh/year) and  is the price of the fuel replaced in the household (£/kWh).

Hence MPBT were calculated for AL-3, AL-1.5 and ST-1.5 collectors. Case 1 presented in Table 5-11 only accounts for the collectors capital cost, assuming that the ICS-SWH was mounted directly into the roof structure.

Table 5-11: Case 1 - Collectors MPBT depending on auxiliary heating system for a 3m2 system

| Collector type | Aluminium3mm | Aluminium1.5mm | Stainless-steel 1.5mm |
| --- | --- | --- | --- |
| Collector cost (£) | 483 | 243 | 1056 |
| Auxiliary heating: Gas |  |  |  |
| Annual savings (£) | 40 | 40 | 37 |
| MPBT(years) | 12.2 | 6.1 | 28.4 |
| Auxiliary heating: Electricity |  |  |  |
| Annual savings (£) | 134 | 134 | 126 |
| MPBT (years) | 3.6 | 1.8 | 8.4 |

Partially replacing a gas heating system with an ICS-SWH would result in a maximum annual saving of £40, while replacing an electric heating system would result in savings up to £134 as shown in Table 5-11 above. As expressed earlier, the MPBT depends on the auxiliary heating system replaced by the ICS-SWH. Replacing an electric, compared to a gas heating system, would be more profitable; increasing the MPBT by 70% for each ICS-SWH.

However, assuming ICS-SWH capital costs including all the components for installation, suggested in Case 2, resulted in increasing MPBT of 23, 39 and 57% for the ST-1.5, AL-3 and AL-1.5 respectively as shown in Table 5-12.

Table 5-12: Case 2 – Overall ICS-SWHs MPBT

| Collector type | Aluminium3mm | Aluminium1.5mm | Stainless-steel 1.5mm |
| --- | --- | --- | --- |
| Collector price (£) | 798 | 558 | 1371 |
| Auxiliary heating: Gas |  |  |  |
| Annual savings (£) | 40 | 40 | 37 |
| MPBT (years) | 20.1 | 14.1 | 36.8 |
| Auxiliary heating: Electricity |  |  |  |
| Annual savings (£) | 134 | 134 | 126 |
| MPBT (years) | 5.9 | 4.2 | 10.9 |

It was observed that the lower the collector capital cost; the higher becomes the impact on the MPBT by adding further costs for each ICS-SWH. Replacing an electric compared to a gas heating system suggested the same MPBT improvement of 70% for each ICS-SWH.

In both MPBT studies the AL-1.5 ICS-SWH was found as the most viable solution reducing MPBT by 50% and 79% compared to an AL-3 or a ST-1.5 system respectively for Case 1 and 30% and 62% for Case 2. An estimated 20 years life time would make the ST-1.5 ICS-SWH a less attractive or viable alternative with an gas heating system; as the customer would not see a monetary payback until after 36.8 years.

The payback time detailed in Tables 5-11 and 5-12 only accounted for capital costs. Some ICS-SWHs may experience operational and maintenance costs associated with certain component failures over the 20 year period, such as deficient valves and problems related to the ICS-SWH itself such as glazing breakage, seal failure, insulation degradation or connection failure. The MPBT when these costs are included would be in the range of 15 to 30 years depending on the aluminium ICS-SWH installed and the fuel being replaced.

## Comparison with other systems and limitations of the study

Many authors have investigated the benefits of LCA of solar collectors and comparative analysis of different collectors types by Asif et al (2006), Tsilingiridis et al (2004), Mirasgedis et al (1996), Crawford et al (2004), Ardente et al (2003) and Ardente et al (2005a & 2005b). However, assumptions and data references are often unclearly stated such as Battisti and Corrado (2005) making comparison between studies difficult. Furthermore, this is compounded by use of aggregated indices such as Tsilingiridis et al (2004).

In addition, the same collector used in this study would have a different eco-profile depending on its location. Scotland having a specific solar climate, a location with greater solar radiation potential would result in a better eco-profile of the ICS-SWH by achieving more energy savings and therefore further reducing carbon emissions.

## Concluding remarks

A comparative study between a stainless-steel and two aluminium ICS-SWH using LCA techniques and a monetary analysis were undertaken in this study. Of the two identical collector units (ST-1.5 & AL-1.5) investigated during this study the aluminium ICS-SWH was found to be more efficient at transferring heat to the water. Of the two materials, aluminium was the better option mainly because of its high thermal conductivity resulting in higher energy savings but also because of its lower environmental impact due to its lightness and the spiralling price of stainless-steel. The potential energy savings associated with using these ICS-SWHs are quite substantial and could reduce annual energy consumption in the home by up to 40% in a Scottish climate by using aluminium ICS-SWHs. The monetary analysis demonstrated that the ST-1.5 ICS-SWH was not a viable alternative as the customer would not have any significant economic benefit over its estimated life time of 20 years. However, it confirmed that the AL-1.5 ICS-SWH was the most financially viable alternative. It should also be noted that prototype prices are always more expensive than large scale manufacturing costs. Another advantage of recommending the AL-1.5 as the best alternative would be its low weight of 10kg apt to fulfil the UK manual handling limits of 25kr/person under the Health and Safety. Issues about the durability of aluminium compared with stainless-steel might arise. However, based on the ICS-SWH estimated life time of 20 years, aluminium can satisfactorily last this time period.

It can be seen that AL-1.5 ICS-SWH definitively offers a significant potential for energy savings and CO2 mitigation. Although the energy and the CO2 payback times for present-day systems are still relatively high, it is generally lower than their expected life time. Future work could be carried through CFD analysis for a multi-fin aluminium ICS-SWH of 1.5mm thickness based on results from Chapter’s 4 and 5 to further improve performance.

Finally, the ICS-SWH studied being at its prototype stage, it would be of interest to research how it could be integrated into recent advances in roof structures in Scotland.

# INTEGRATION INTO HOUSING DESIGN

In order to understand how to best integrate the ICS-SWH prototype into dwellings, an insight of government incentives towards the incorporation of LZCT and their development into legislative provision and zero-carbon houses is given. Best construction practice of such dwellings is also presented to show how technology such as SWH can help in achieving zero-carbon homes. The integration of SWH’s depends on the type of application. Typical SWH installations into domestic hot water systems are described in order to suggest the most suitable installation practice. Finally, the integration of the ICS-SWH into roof structures is discussed in order to give an overview of the potential integration of the system with modern modular methods of construction (MMC).

## Towards zero-carbon homes

This section will focus on the different government initiatives and legislative provision towards the development of zero-carbon houses.

### UK Government Initiatives

      - Energy Performance of Building Directive - EU

The Energy Performance of Buildings Directive (EPBD) came into force on January 2003 with the objective to improve the energy efficiency of buildings within the EU through cost-effective measures and has therefore important implications for the owners, operators and developers of all buildings in the UK.

The EPBD required all EU members to take measures to ensure that minimum energy performance requirements were set for new buildings and for large existing buildings when they are refurbished. This influenced UK Building Regulations limiting the overall annual CO2 emissions of new buildings to a maximum target level; established by reference to the calculated emissions from a notional gas-heated building of the same size and shape as the proposed building.

The most visible impact of the EPBD results in the implementation of energy performance certificates, which need to be prepared when buildings are constructed, sold or rented since October 2008. The certificates classify buildings on a scale from A (best) to G (worst) based on annual CO2 emissions per unit floor area therefore providing an indicator of energy performance of the building.

Another aspect of the EPBD would be the provisions for regular maintenance inspections of heating and cooling plant in order to provide adequate advice for the operation of the plant.

Incorporation of LZCT is not compulsory for compliance with the regulations, however the target being expressed in terms of CO2 emissions, the choice of fuel is significant as different fuels give rise to different CO2 emissions for a given quantity of heat produced. This would results in encouraging the development of LZCT for buildings to reduce the building’s net demand for fuel.

The Energy Performance of Buildings Directive (EPBD) is thus a driving legislation with an objective to reduce building energy use and encouraging the development of LZCT for buildings.

      - Code for sustainable homes

The “Code for Sustainable Homes” is the legislative backbone in the construction of new homes in the UK which was implemented in May 2008 in England and Wales and will form the framework for Scottish building standards. Prior to this an EcoHomes Building Research Establishment Environmental Assessment Method (BREEAM) was in use although with no legislative mandate. Both tools are used to assess the environmental performance of new buildings over their entire service life while only EcoHomes BREEAM assess existing buildings.

The Code measures the overall sustainability performance of a new home using a 1 – 6 star rating system based on the Communities and Local Government (CLG) (2006) publication. The code divides the house into nine different categories such as Energy/CO2, Water, Materials, Surface Water Run-off, Waste, Pollution, Health & Wellbeing, Management, and Ecology; each category has points awarded. The higher the score in the rating system, the higher the sustainability rating of the house.

The step-by-step approach of the Code makes it an effective tool towards sustainable housing. Level 1 is set just above the current 2006 building regulations while level 6 would have very high mandatory heat loss parameter standards resulting in an increased demand on the building envelope such as insulation, glazing and shading and how these operate with the technological systems of the house to achieve zero carbon. Level 3 standard of the code will become mandatory at the beginning of 2010, while level 4 and level 6 will be phased-in in 2013 and 2016 respectively.

Long term government objectives for this Code are to make it the single national standard for the design and construction of homes and for it to drive a step-change in sustainable home building practice. The Government has also indicated its intention to use the Code as the basis of future Building Regulations as stated by CLG (2006). The Code became mandatory in May 2008 for all new private sector homes and will be a major help in trying to achieve the government’s objective of zero-carbon dwellings by the year 2016.

      - Stamp Duty Land Tax (SDLT) relief

Following the government’s objective of achieving zero-carbon homes by the year 2016, last year’s Budget Report published by HMRC (2007) announced that all new zero-carbon homes would be exempt from stamp duty land tax on the house. The SDLT is a transaction tax payable on the purchase of land and property to be paid by the buyer at a rate which depends on the purchase price of the property. The zero-carbon home standard is measured by use of the Government’s Standard Assessment Procedure for the energy rating of dwellings (SAP). The relief is only available to the first newly built zero-carbon home sale and does not apply to the second or subsequent property sales. It is only valid for private residential individuals and not for commercial businesses and has a time limit of five years, after which time the scheme will be reviewed. The relief provides exemption from the SDLT tax when a house costs less than £500,000, and provides a £15,000 reduction to all homes worth more than £500,000.

The main objectives of introducing stamp duty relief on zero-carbon homes is to help launch their concept and create a market for them, to support micro-generation technologies and enhance public awareness of the benefits associated with such homes. It also provides an incentive for developers to build zero-carbon homes through stimulating consumer demand by advertising them as free of stamp duty land tax. This incentive would also help the UK to achieve a 60% cut in carbon emissions by 2050 as stated by HMRC (2007).

The SDLT relief therefore enhances and encourages the construction of homes incorporating specific energy efficiency standards in the fabric of the building and micro-generation technology’s at the design stage.

### Zero-carbon housing for UK

Government initiatives and incentives offer developers the possibility to integrate sustainable construction and renewable energies into new developments. A zero-carbon home is defined by HMRC (2007) as:

“One that does not consume fossil fuels for heat and power. It is highly insulated and uses renewable energy to power its needs over a year through micro generation. It will draw from the grid when the micro generation is insufficient but could sell excess generation back to the grid.”

Good and best practice examples of low and zero-carbon developments were identified and are introduced. An organisation, Zero Energy Development (ZED) factories recently introduced their innovative housing system Rural ZED to the zero-carbon housing sector at Ecobuild (2008). Rural ZED is designed as a three bed detached dwelling that catches fresh air, rain and sunlight allowing a full integration of renewable micro-generation technologies which brings it to a Zero Energy Development. Electricity is generated from solar photovoltaic (PV) panels on the roof, and where the site is suitable, a roof wind turbine. Water heating is generated from roof mounted SWH, backed-up in winter by a biomass boiler.  Rural ZED achieves Code level 4, but provides an upgrade path to level 6, depending on the budget available. The higher code levels will necessarily be achieved at a higher cost.

BRE Innovation Park OFFSITE (2007) demonstrated various types of near zero and zero-carbon homes designed and built by various companies including Kingspan, Stewart Milne and Hanson. The Lighthouse, created by Kingspan Offsite was the UK’s first zero-carbon house to meet Code level 6. Like the Rural ZED, the Kingspan Lighthouse was designed as a two or three bed detached dwelling using efficient construction methods, energy use to achieve low CO2 emissions and carbon footprint. The pitched roof at 40˚ possess an inbuilt wind catcher/light funnel and accommodates solar PV generating most of the electricity needs while a SWH generates hot water. The building fabric and building envelope delivers a thermally insulated and air tight home that will only need heating during winter months. The Sigma House of Stewart Milne Group and Hanson Ecohouse were designed as a four and three bed detached dwellings and met Code level 5 and level 4 respectively. They incorporate a roof light and micro-generation technologies similar to other zero-carbon homes. Figure 6-1 show the different low and zero-carbon developments described above.

| c | d |
| --- | --- |

Fig. 6-1: Towards zero carbon homes: a. RuralZED, b. Ecohouse, c. Lighthouse, d. Sigma

Efforts have been made by developers to integrate sustainable construction and micro-renewable energies into new developments. Micro-renewable technologies have a strong role to play in the development of zero carbon housing. Solar water heaters have been installed in all best practice examples of low and zero-carbon developments shown above; suggesting that there is a strong potential for this type of technology to participate towards zero-carbon homes. An insight into this technology, and particularly that of flat-plate collectors is provided in the next section.

## Flat-plate collectors for low carbon construction

In order to understand the principles of operation and integration of this technology the predominant types of installation of flat-plate collectors are presented.

### Existing flat-plate collectors

Six recognised companies, AES Solar Ltd, Amplifaire, Energy limited, Solar Power Scotland, Renewable Devices Energy Solutions Ltd and Solar Energy systems, were approached to provide typical installation details for SWH in the UK, however only three gave an insight of the type of installation in use. Their installation systems are described below.

      - Solar Energy Systems

A frequently adopted alternative used by Solar Energy Systems is to use a solar pre-heat tank which has no input from the back-up heat source (boiler). The system uses an open-vented system resulting in an un-pressurised installation. Cold water from the main enters the water reservoir in which a ball valve controls the level of water. Cold water is then fed to the bottom of the solar pre-heat tank each time hot water is drawn-off by the household. The water is pre-heated by the indirect SWH primary circuit in which the heat transfer fluid passes and circulates to the heat exchanger and back.  The pre-heated water then feeds the downstream hot water tank connected to the boiler to achieve the desired hot water temperature supply as shown in Figure 6-2.

Fig. 6-2: Separate solar tank pre-heating the dwelling hot water tank

The SWH primary circuit used for pre-heating is isolated from the consumed water hence allowing the use of anti-freeze. This system is more expensive; requiring two tanks, has a high space requirement and takes a longer to install.

      - AES

AES is one of Scotland’s most recognised solar system manufacturers and provides a number of different SWH installation types. All their systems use an indirect sealed primary circuit in which the heat transfer fluid that passes through the SWH is isolated from the consumed water by a form of heat exchanger and hence allows the use of anti-freeze. A sealed primary system results in a significant rise in static pressure by the filling process, typically for solar DHW between 1 and 3 Bar over atmospheric pressure as stated by CIBSE (2007).

The first proposed installation consists of a double-coil installation or combined solar-dwelling hot water tank. A schematic of the system is shown in Figure 6-3. Cold water from the mains enters the bottom of the water tank which is fitted with two indirect coils both working as heat-echangers, one heated by the SWH, the other heated by a boiler. Outputs of the back-up (boiler) and the SWH systems are both into one water tank. This type of installation is another frequently adopted alternative in the UK.

Fig. 6-3: Combined solar dwelling hot water tank.

Another method would be to use an external heat exchanger. As previously, cold water from mains enters the bottom of the water tank but also goes to a secondary pre-heated circuit. The secondary circuit goes into an external heat-exchanger in transferring the heat from the primary SWH to the secondary circuit going back to the water tank. The water uses a back-up circuit to deliver the hot water supply. Each circuit requires a pump resulting in higher final costs. A schematic of the system is shown in Figure 6-4.

Fig. 6-4: External heat exchanger

Another installation proposed by AES consists of a combi-boiler solar compatible installation shown in Figure 6-5. Cold water from the mains enters the bottom of the water tank to be pre-heated by the SWH primary circuit used as a heat-exchanger. Each time hot water is drawn from the household the pre-heated water goes to an instantaneous heating appliance such as a combi-boiler which uses a thermostatic blending valve to protect the cold supply of the combi-boiler.

Fig. 6-5: Combi-boiler solar compatible installation

      - Solartwin systems

The Solartwin system is a more recently adopted alternative using a direct solar system installation. The SWH system shares the same open-vented safety system and cold water reservoir with the water tank.

The SWH system employs a flexible pipe in the absorber plate resisting the volumetric expansion due to freezing. The SWH system is therefore freeze-tolerant and can use mains water as a heat transfer fluid. The collector and circulation system can therefore be plumbed directly into the existing hot water system. The use of a small pump powered by a photovoltaic module provides a low and variable flow enhancing storage tank stratification as stated by Grassie et al (2001) and results in a net zero carbon system. A schematic of the system is provided in Figure 6-6.

Fig. 6-6: Solartwin system

This system reduces costs as it requires minimal plumbing and additional components required to prevent frost damage in the above systems are no longer necessary. It is also easier and quicker to install and has an additional thermal benefit through heating the domestic hot water directly.

### Suggested installation for the ICS-SWH

Based on the typical commercial SWH installation detailed above, constraints for the installation of the ICS-SWH under study were considerated and an optimised installation proposed.

      - Installation considerations

The solar water heater under study stores the solar heat directly in its integrated tank allowing the heat to build-up slowly during the day. Using the ICS-SWH as both the collector and storage tank significantly reduces the space requirements and costs associated with typical SWH installation as it would use main water.

The primary issues concerning the ICS-SWH installation would be the potential freezing problems and pressurisation of the system. The system uses mains water as the heat transfer fluid and could potentially freeze during winter months. Using a sealed system would result in a significant increase static pressure between 1 - 3 Bar over atmospheric pressure.

In extreme weather conditions, freezing could damage the ICS-SWH. Grassie (2001) suggested the use of flexible ethylene propylene diene M-class rubber or EPDM rubber instead of the more commonly used copper pipes. Using this material allows pipes to expand during freezing periods therefore reducing potential damage. The ICS-SWH could be designed to use EPDM rubber inlet and outlet pipes where the greatest potential for freezing occurs. An additional benefit in using EPDM rubber inlet and outlet pipes would be the avoidance of galvanic corrosion occurring between aluminium and commonly used materials for water heating pipes such as copper, brass and stainless-steel.

Using a sealed direct system would result in pressures of up to 3 Bar that the ICS-SWH may not withstand. A pressure regulation valve and a pressure relief valve could then be integrated in the installation to regulate the water pressure on entry to the ICS-SWH and relieve excess pressure due to expansion.

      - Proposed ICS-SWH installation

The system would consist of a direct sealed installation using mains water as a heat transfer fluid that passes through the SWH incorporating a back-up heat source to provide required domestic hot water final delivery temperatures. A combi-boiler solar compatible installation or direct electric heater, such as Titan 66 tankless hot water heater, would be then integrated into the system as a back-up heat source. Smyth et al. (2001) suggested that most ICS-SWHs have large thermal masses and simple compact structures which give good general resistance to freezing climates. Further studies in order to integrate tolerance to freezing are required for this system. Initial discussion suggest a flow regime induced within the ICS-SWH and the use of  flexible inlet and outlet pipes capable of resisting the volumetric expansion due to freezing and reducing the risk of galvanic corrosion.

Water quality is of primary importance if the water is being used directly from the ICS-SWH. Limescale is a common phenomenon occurring in hot water storage systems indirectly or directly connected to the solar water heater. The main component of limescale deposited in water heaters consists of calcium carbonate which is soluble in water. However, at temperatures above 70(C the soluble bicarbonate is converted to poorly soluble carbonate leading to deposits in the water heater usually resulting in a life and performance reduction of the system. There are many ways to prevent limescale. Products such as “Ecoflow” are reported to prevent limescale at the source. It consists of a magnetic water conditioner fitted on the rising main where water comes into the home providing a constant supply of magnetically treated water. The sterilisation of bacteria such as the legionella bacteria in hot water systems is also of primary importance for Health and Safety approval of the ICS-SWH. Temperatures of consumable water are generally between 20(C and 46(C according to CIBSE (2002) when storing heat, thus providing adequate conditions for the multiplication of bacteria. The treatment of the pre-heated water from the ICS-SWH therefore cannot be considered suitable for distribution as domestic hot water until fully treated. At 60(C, bacteria can survive for only minutes whereas at 70(C the bacteria in the water are killed instantaneously. A flow limiter would be required in the case of an instantaneous heating appliance such as the ICS-SWH in order to maintain the target treating temperature. A thermostat interlocked to the instantaneous heating appliance will also ensure that all water draw-off reached the target temperature. A schematic of the system is shown in Figure 6-7 including the components below:

- Pressure regulator valve

- ICS-SWH

- Pressure relief valve / Air vent

- Thermostatic mixing valve

- Instantaneous heating appliance

- Thermocouple

Fig. 6-7: ICS-SWH installation

When hot water is drawn off from the ICS-SWH, mains cold water controlled by a pressure regulated valve is fed to the bottom of the ICS-SWH flushing out the hot water from the top of the collector passing through a pressure relief valve. The hot water then goes to an instantaneous heating appliance such as a combi-boiler or electric heater to deliver the desired temperature of hot water supply.

This system would reduce costs as it requires minimal plumbing; it is of simple construction and heats the domestic hot water directly using no separate water tank. Supposing that the ICS-SWH was integrated in a zero-carbon house, the electric instantaneous heating device could be powered by micro-renewable technologies; therefore resulting in a zero-carbon system.

## Integration of the ICS-SWH into roof structure

Integrating solar water heaters into roofs depends considerably on the roof type and the design of the solar water heater installed. Most solar water heaters in UK are mounted above the roof covering using brackets to hold the collector to the roof structure. The roof is therefore altered from its original design loading which might cause structural and durability issues. Solar water heaters can also be vertically mounted or integrated directly into the roof covering but this would require specialist structural advice. Penetrations for bracketry and water connection also compromise the roof integrity.

Current estimates from the Parliamentary Office of Science and Technology – POST (2003) assert that there will be three million new UK households by 2016. The UK government is encouraging a modern modular method of construction (MMC), which it says can achieve “a step change in the construction industry to produce the quantity and quality of housing we need” as stated by POST (2003).

In order to provide the best practice to integrate the ICS-SWH in future households, an overall  insight of MMC and more specificallyan example of this, the structural insulated roofing system (SIRS) developed by a Scottish based company Donaldson Timber Engineering (2007) is presented to demonstrate its integration.

### Modern Method of Construction (MMC)

The recent interest in MMC for housing construction is driven by a growth in the number of households in the UK. MMC, also known as prefabrication, consists of the manufacturing of house parts off-site in factories. While issues have arisen regarding the quality of houses, recent technical improvements in prefabrication including innovative site-based methods and the wide range of material used, suggests that MMC has many advantages with potential benefits described by POST (2003) such as:

- faster construction

- fewer housing defects

- energy efficient houses

- reductions in energy use (less transport)

- less waste production

- safer working conditions

- lower impact on local residents during construction

The two main products of MMC consist of modules and panels. Modules, also known as pods, consists of ready-made rooms, usually bathrooms or kitchens where all the fittings and services are added in the factory. Ready-made rooms are then assembled together to produce a whole dwelling. Panels consist of ready made walls, floors or roofs.  These are transported to the site and can often be assembled within a day as stated by English Partnership (2007).

### SIRS Roofs

The SIRS roof (Structural Insulated Roof System), manufactured by Donaldson Timber Engineering (DTE) is an example of modular offsite roof design, employing modern methods of construction MMC. The SIRS roof is a roofing system that has been developed to provide a safe and cost effective solution in delivering additional space such as room in the roof in a domestic dwelling.

The SIRS roof design parameters exceed current building regulations in terms of insulation, and comply with government directives on modern methods of construction.

The SIRS system suits a variety of roof shapes and is manufactured using timber from sustainable sources. It also contributes to Low Carbon Build and has been approved by the NHBC (National House-Building Council) last July 2007. The SIRS roof assembly is shown in Figures 6-8 and 6-9.

Fig. 6-8: Structural Insulated Roof System - SIRS, Wood (2006)

Fig. 6-9: Structural Insulated Roof System, James Johns roof trial.

The design flexibility of the SIRS roof would allow the direct integration of the ICS-SWH on the roof panel. This would result in a faster and safer integration of renewable technology through off-site construction and high insulation of the ICS-SWH due to the excellent insulation performance of SIRS.

### Structural issues

There are many structural issues when considering the installation of a SWH system. The additional load of the mounted ICS-SWH requires specialist structural advice. However, directly integrating the ICS-SWH into the roof covering replaces tiles thereby reducing weight issues. For instance, the Sandtoft company (2008) provides a range of clay tiles weighing between 34-72kg for a 1m2 area resulting in an average weight of 53kg/m2. When integrated into the roof covering the filled 1m2 AL-1.5 ICS-SWHs weighs 41.3kg which would result in a 22.1% weight reduction over clay tiles.

A structural engineer would normally be responsible for calculating such loads. As a result of high wind speed, steeper pitched roofs are generally installed in Scotland to diminish the potential for tiles lifting.

Whether the installation is mounted above the roof or directly integrated into the roof covering, a flashing system would be required to make the installation weatherproof. An overview of VELUX (2005) flashing systems is given as suitable method for the ICS-SWH integration in roofs. VELUX flashings ensure weathertight installation of all VELUX roof windows by ensuring safe water drainage from the roof above the window. VELUX (2005) uses prefabricated flashing systems which overlap with the roof covering to provide a weathertight finish around roof windows. VELUX flashing systems are compatible with most types of roofing material and allow a discrete installation as the roofing material covers the top and side flashing components. Flashing materials are weather-resistant. A collar ensures a tight connection between the roof window and the membrane and weather tight joints are created by overlapping the flashing components whilst the foam gasket creates a seal between the flashing and the roofing materials. Another feature of VELUX flashings is the incorporation of tile support ensuring that the roofing material remains in the right inclination above the roof window. A pleated apron is then dressed to form a tight seal underneath the window in a profiled roof. Figure 6-10 shows a VELUX installation.

Fig. 6-10: Installation schematic and final installation of VELUX windows, VELUX (2005)

The general good practice introduced by CIBSE (2007) in respects of pitched roof guidance is:

- To maintain access to the roof covering below the solar water heater

- To report loads onto the roof covering

- To design the loads onto substantial roof structures such as trusses

- To provide sufficient lap of flashing where tiles are cut or raised

- To consider negative pressure lifting adjacent components such as tiles

Based on these parameters, the integration of the ICS-SWH was considered and simulated.

### Integration of the ICS-SWH

The integration of any SWH has a direct impact on a building including its performance and aesthetics. Integrating an ICS-SWH should not devalue the property and should comply with building regulations and planning.

Using VELUX methods for weatherproofing the ICS-SWH in a SIRS roof structure could ensure a good integration of the ICS-SWH in a roof covering. However there are issues concerning the direct integration of the ICS-SWH into the roof covering. The viability of such integration should be studied further in order to ensure its feasibility.

## Concluding remarks

This chapter explored the potential installation and integration of the ICS-SWH under study into recent advances in constructions practice. Recent governmental initiatives towards the expansion of zero-carbon development enhanced the integration of micro-generation technologies into buildings. The best practice examples of low and zero-carbon developments such as the Kingspan Lighthouse or RuralZED identified the potential for roof mounted SWHs to generate a dwellings water heating with a heating back up and their contribution towards such zero-carbon developments. Best SWH installation practices of three Scottish companies were studied in order to provide an optimum practice for the ICS-SWH installation. The suggested installation consisted of a direct sealed system using mains water as a heat transfer fluid and an instantaneous heating back-up source such as a Titan 66 tankless hot water heater.

The integration of the ICS-SWH in future potential Scottish household is a final milestone of the research project. Integrating an ICS-SWH should not devalue the property and should contribute to complying with housing codes and legislations. Modern methods of construction and more precisely of structural insulated roofing system (SIRS) were recently introduced as contributing to Low Carbon Build. The design flexibility of the SIRS roof could allow the simulated direct integration of the ICS-SWH inside the roof panel. Such installation results not only in faster and safer integration through off-site construction, but also in higher performance of the ICS-SWH due to the high insulation performance of SIRS. Such installation would also provide a substantial value to developers proposing such pre-integrated micro-renewable systems to customers resulting in achieving higher levels of the Code for Sustainable Homes.

In conclusion, this section of the thesis opens an avenue for future work on ICS-SWH integration but also shows the potential of ICS-SWH in the solar water heating and zero-carbon home markets.

# CONCLUSIONS

Energy plays an essential role in society and human life, driving economic development and the wellbeing of society. Modern societies use more energy every year for industry, services, homes and transport resulting in increased environmental concerns associated with fossil fuel consumption and production. Ensuring a secure, clean and affordable supply of energy is essential towards the sustainable development of a modern society. The domestic sector is the largest consumer of energy in the UK with 80% accounting for space and water heating. Hence, there is good potential scope for addressing domestic energy requirements, particularly for hot water, from renewable sources. Solar water heating systems have real potential in Scotland due to the higher annual heating loads allowing longer and greater savings using solar thermal energy. A review of many years of research on solar water heating systems has outlined the promising approach of integrated collector storage solar water heaters (ICS-SWH) in northern hemisphere applications due to their good overall performance in overcast sky conditions. ICS-SWHs are one of the simplest types of SWH on the market incorporating the solar collector and thermal storage tank in a single unit making them relatively affordable with low costs. There was therefore a need to estimate the potential of ICS-SWH for the northern climates.

This research was conducted with the primary goals of developing an affordable, optimised and feasible ICS-SWH prototype for Scottish weather conditions and to develop a new tool to model ICS-SWH performance. The approach involved laboratory and field tests of the ICS-SWH, performance modelling for laboratory and field conditions, performance optimisation through CFD modelling, life cycle assessment and monetary analysis of the ICS-SWH and finally the analysis of potential benefits and integration into buildings of this ICS-SWH prototype.

## Summary of conclusions

Significant points that can be drawn from the research analyses are as follows:

Laboratory and field experiments

- The methodology adopted in this study was generally more accurate and rigorous than previous studies.

- The incorporation of extended surfaces in the ICS-SWH was analysed and suggested an increase in heat transfer and water stratification in the ICS-SWH as well as providing structural strength to the collector. Incorporating fins in the collector resulted in an increase in heat transfer of 18% in the stainless-steel ICW-SWH. Using a more conductive material, such as aluminium, resulted in a 13% increase in water temperature.

- Analysis suggested that the temperature stratification profile results in differential buoyancy forces in the fluid causing convection by gravity. It also indicated that this depends upon the incident solar radiation, the exposure time and collector material, given a constant angle of inclination of the ICS-SWH. A polynomial function for the stratification profile for each hour could then be developed taking heat flux and longitudinal location in the collector as the main parameters.

- The benefit of selecting aluminium for the ICS-SWH was clearly supported by the current laboratory findings; showing it out-performing the stainless-steel ICS-SWH with an overall increase in the aluminium ICS-SWH efficiency of 6% over an eight hour time period.

Although the collector was tested in a laboratory with calibrated instruments, the actual performance of the ICS-SWH under real weather conditions yielded important results on assessing the viability of the aluminium ICS-SWH and are summarised below.

- Parameters such as thermal mass of the system, orientation, cloud cover and sky temperature were found to significantly influence the ICS-SWH performance in field weather conditions, and should not be neglected.

The thermal mass was found to play an important role in the effectiveness of the system as it affected the heating charge and cooling discharge operations of the collector and the amount of stored thermal energy. The water stored in the collector chiefly contributed towards the thermal mass of the system with a value of 208.3kJ/K compared with the aluminium and stainless-steel material of heat capacities of 17.2 kJ/K and 13.3kJ/K respectively. This shows the ability of a given water volume to store internal energy while undergoing a given temperature change.

It was also observed that a decrease in incident solar radiation for a relatively long period of time can lead to significant losses and decrease in stratification rate, therefore positioning of the ICS-SWH is of primary importance to achieving good performances.

The effective sky temperature can be about 10-20 degrees Celsius below ambient temperature at ground level with clear sky conditions and close to, or just below, the ambient temperature during cloudy conditions. It was therefore concluded that cloud cover should not be neglected as it affects the cover temperature through radiation losses and therefore the final water temperature output of the ICS-SWH.

- The draw-off study showed that the ICS-SWH was able to maintain temperature stratification when draw-off occurs, a crucial factor in maintaining good performance of the ICS-SWH. It was also observed that draw-off actually increased the overall thermal longitudinal stratification, thus improving the overall performance of the ICS-SWH. Average draw-off temperatures recorded at peak demand hours suggest that the ICS-SWH could cover 55%, 66%, 83% 72% of the hot water demand at 8:00, 9:00, 19:00 and 20:00 respectively based on a delivery temperature of 55°C. A strong relationship between water drawn-off, water temperature stratification, solar radiation and outlet water temperature achieved in the collector was reported.

- In addition to the relative importance of different parameters influencing the ICS-SWH performance developed in this study, the current conventional standard procedure used by the ESCSTG (1989) for predicting the effectiveness of ICS-SWH was found not to be representative of the actual system performance as thse assume steady state conditions. This emphasised a need for new methods to predict water temperatures and performance of ICS-SWH.

Modelling ICS-SWH performances

- Two macro models - laboratory and field - were developed in this study to predict the performance of ICS-SWHs at any location and with different installation configurations. Each macro model resulted in a thermal energy simulation model which analysed combined heat flux environmental networks within the ICS-SWH.

- The laboratory macro-model was able to predict the bulk water temperature in different ICS-SWH configurations using different construction materials for a given heat flux, ambient temperature, inlet water temperature and resultant stratification profile over time.

The role of extended heat transfer surfaces (fins) were modelled and showed good improvement by achieving higher bulk water temperatures. Effective fin heat transfer rates were enhanced by the choice of a material e.g. aluminium over stainless steel. The improvement was found to be 67.3% and 63% for aluminium fins of 3mm and 1.5mm thickness and 25.3% for 1.5mm thick stainless-steel.

An improvement factor (IF) measuring the improvement achieved by using fins in the ICS-SWH was developed. By increasing the thickness of the fins the overall IF improved by 3.5%, while changing to a more conductive material the IF improved by 5.5%. The greatest improvement factor was achieved for the aluminium ICS-SWH with a 3mm fin thickness.

The computational results from the model were found to be in close agreement with the experimental data. Satisfactory curve fits were obtained for the water temperatures, achieved experimentally and numerically for all the ICS-SWH types. Testing the results using statistical methods resulted in very low MBE and RMSE values; validating the ability of the model to predict the water bulk temperature in the ICS-SWH.

Longitudinal stratification of temperature within the solar collector was modelled using the mean bulk water temperature computed by the macro model, the given heat flux and the total time of exposure. The stratification model was developed using polynomial functions previously developed via experimental data for 100, 200 and 400W/m2. Different heat inputs outside the normal experimental range were then simulated in order to validate the model. Results for 50, 150, 250, 350 and 600W/m2 over a period of eight hours (simulating a typical day of operation) demonstrated that experimental and computer simulation results were in good agreement. The MBE value of 1 Celsius showed that the model had a tendency to slightly under predict its computed value. Statistical results validated the accuracy of the model to compute bulk water temperature.

- The field macro thermal model developed was found to be suitable for predicting bulk water temperatures under real weather conditions and therefore more predictable ICS-SWH performance.

Analysis carried out using data for five and fifty day testing periods between the month of June and July validated the model to predict bulk water temperature inside the ICS-SWH by comparing computed results with experimental data.

It was observed that gradual heating and cooling profiles due to the thermal mass of the system were experienced in the macro model. However, a lower cooling rate of the modelled values was observed for each day. This could be explained by the propagation of errors and uncertainty by the use of regression analysis and assumed weather data; resulting in a decrease in the accuracy of the model.

Experimental water temperature was followed very closely by predicted water temperature although it showed a slight over-estimation of 1.3 and 1.5 Celsius of its computed values by the proposed model for five and fifty day periods respectively. The study also demonstrated the effect of wind velocity on the bulk water temperature and the importance of having accurate wind speeds. Increasing the velocity from 0m/s to 6m/s resulted in an average decrease of 5% of the bulk water temperature.

Although this model only gives mean values of water temperature which, in reality, varies along the longitudinal height of the collector, it gave a good estimation of the ICS-SWH performance. The simulation could be extended resulting in a useful tool to estimate the yearly performance of the ICS-SWH.

- Both simulation models showed that computational results were found to be in close agreement with the experimental field measurements. Statistical methods suggested that both models were robust and could compute bulk water temperature in the ICS-SWH and predict the performance of an ICS-SWH at any location and with different installation configurations.

Optimisation through CFD modelling

- A Computational Fluid Dynamic (CFD) study was undertaken to model flow and heat transfer in the three-dimensional (3D) SWH geometry to provide information about performance of the collector and evaluate design improvements. It was found that 2D analysis was insufficient for any angle of inclination of the ICS-SWH above horizontal as a gradient exists in the longitudinal direction. Hence, based on a 45° inclination of the collector, a 3D analysis was undertaken to estimate an optimum fin spacing to make further improvements on the original four-fin ICS-SWH.

- It was found that one further fin added to the original four-fin ICS-SWH design would improve the heat transfer by 2.3%. It was observed that the five fins supplied more energy to the collector than four at the beginning of the charging process. The intermittent availability of incident solar radiation in Scotland shows high potential for this type of improvement as it is advantageous to have a rapid heating process.

- It was also observed that while the five fins supplied more energy to the collector than four at the beginning of the charging process, additional fins seriously impeded the water flow with a decrease of the velocity in the SWH. This decrease in velocity has a corresponding reduction on the Nusselt number with a consequence that the heat transfer coefficient falls in a predictable manner as outlined by Churchill (1974).

Life cycle assessment and monetary payback

- A LCA and monetary analysis of two aluminium ICS-SWHs of 1.5 and 3mm thickness (AL-1.5 and AL-3) and one stainless-steel ICS-SWH of 1.5mm (ST-1.5) incorporating extended heat transfer surfaces were carried out in order to establish the most commercially viable ICS-SWH with the smallest environmental footprint.

- It was found that despite the high amount of energy to produce aluminium, the “light” and recyclable properties of the material resulted in similar embodied energy when compared with stainless-steel. This resulted in a smaller environmental impact due to lower carbon emissions released to the atmosphere during the production process.

Energy and carbon dioxide savings associated by using those ICS-SWHs were modelled and showed that although the AL-1.5 ICS-SWH was marginally out-performed (0.1%) by the AL-3 ICS-SWH, the fact that it only uses half the volume of material in producion makes it more viable. The carbon dioxide savings showed that, depending on the ICS-SWH installed, there is a potential for saving 6% more kgCO2 per year by using an Al-1.5 compared with a ST-1.5, and only 0.5% by increasing the thickness of a similar ICS-SWH material.

The energy payback times (EPBT) of the ICS-SWHs were found to be consistently lower than three years for all ICS-SWHs with the lowest EPBT value of 1 year 7 months achieved by the AL-1.5 ICS-SWH. This value shows the great energy potential of such an ICS-SWH design. A calculation of the carbon dioxide emission payback times confirms the higher potential of using an AL-1.5 ICS-SWH by decreasing the ECPBT by 42% and 48% when compared with AL-3 and ST-1.5 ICS-SWHs respectively.

The potential annual monetary savings of a 3m2 ICS-SWHs installation vary considerably between homes using fossil fuelled or electric heating systems.

Partially replacing a gas heating system with an ICS-SWH would result in a maximum monetary payback period (MPBP) of 28.4, 12.2 and 6.1 years for the ST-1.5, AL-3 and AL-1.5 respectively considering the collectors’ capital cost only. Assuming ICS-SWH capital costs including all the components for installation resulted in increasing MPBT of 23, 39 and 57% for the ST-1.5, AL-3 and AL-1.5 respectively. In both MPBT studies the AL-1.5 ICS-SWH was found as the most viable solution. The ST-1.5 ICS-SWH was a less attractive or viable alternative when installed in conjunction with a gas central heating system as the customer would not realise any significant economic benefit over its estimated life time of 20 years.

- All results point to the AL-1.5 ICS-SWH as the most viable alternative to operate in Scottish weather conditions. It would therefore be recommended to use an AL-1.5 ICS-SWH for further investigations due to its energy and environmental benefits.

Integration and potential benefits

This section explored the potential installation and integration of the ICS-SWH under study into recent advances in constructions practice and its potential benefits for builders and households.

- It was found that recent government initiatives in the UK help support developers towards the expansion of zero-carbon development and enhanced the integration of micro-generation technologies into buildings. Roof mounted SWHs were found to be installed in many best practice examples of low and zero-carbon developments such as the Kingspan Lighthouse or RuralZED suggesting that there is a strong potential for this type of technology to participate towards zero-carbon homes.

- Based on the predominantly installed commercial types of flat-plate collector in Scotland, best practice for installing the ICS-SWH appeared to be a direct sealed installation. This installation would use mains water supply as the heat transfer fluid backed-up by an ‘instantaneous’ in-line heat source for periods of low insolation or as top-up heating provision.

- Potential for integrating the ICS-SWH in future Scottish dwelling design was a final milestone of this research project. It was found that modern methods of construction and, more specifically, examples of structural insulated roofing system (SIRS) or Structural Insulated Panels (SIPS) were recently introduced as contributing to Low Carbon Build and could allow the direct integration of the ICS-SWH inside the roof panel. Thus contributing to complyiance with planning and building regulations. Such installation would result not only in faster and safer integration, through off-site construction, but also in higher performance of the ICS-SWH due to the high insulation performance of such roof systems. This would also provide a substantial value to developers proposing such pre-integrated micro-renewable systems to customers resulting in achieving higher levels of the Code for Sustainable Homes.

## Contribution to knowledge

Original contribution within the context of the presented research can be identified in the following sub-sections:

Innovation:

The collector investigated is a new prototype enhancing the thermal efficiency of the ICS-SWH through the use of more efficient materials while lowering the capital costs down to the order of £300 compared to commercially available collectors priced at over £2500.

Methodology and feasibility:

Laboratory and field experiments provided detailed information of the ICS-SWH behaviour in different situations. The field experiments showed the feasibility of such heaters in Scottish weather conditions. Typical annual savings of 1106 kWh can be achieved for a 3m2 domestic system corresponding to a maximum annual saving of £40 while partially replacing a gas heating system with an ICS-SWH, and up to £134 while replacing an electric heating system.

New predicting tool:

The innovative modelling tool developed can predict the bulk water temperature of the ICS-SWH for any location in the world and therefore predict the ICS-SWH performance. ICS-SWH design parameters can be changed by the user for their own research resulting in an evolving programme.

Design improvement & Costs:

Improvements of the ICS-SWH design were suggested through the CFD analysis while keeping the costs to a minimum.

Viable prototype:

The ICS-SWH prototype showed a high commercial potential due to its environmental and monetary benefits resulting in a viable commercialisation of the prototype. Improvements to the ICS-SWH design were also suggested through the LCA while lowering the capital cost of the final unit.

Viable installation:

The ICS-SWH prototype showed potential for integration into commonly used solar water heating installations which could result in a viable installation. This type of installation could use an electric instantaneous hot water heater as an instantaneous back-up heater.

Market value:

The ICS-SWH was shown to have a real market value. To date, there is no commercial ICS-SWH on the solar thermal market resulting in a niche product. The confidence in the design resulted in patenting the ICS-SWH. The ICS-SWH could also have a high market value when integrated into modern methods of construction such as roof panels.

## Potential future work: Looking back, looking ahead

The avenues for possible future research can be classified as follows:

Thermal macro model potential improvements

The thermal macro model developed could be implemented in the Visual Basic program and could provide a better user interface. Further improvements of the thermal model could be incorporated. The thermal stratification model could be developed for real weather conditions. Other improvements such as the modelling of water draw-off could be integrated.

Further CFD modelling

In light of the CFD modelling results presented, the five-fin collector performed generally better than the original four-fin collector. Therefore, this design could be suggested as a new arrangement for the collector assuming that the addition of one fin has a very low additional cost. The LCA study also recommended the use of an aluminium ICS-SWHs of 1.5 thickness incorporating extended heat transfer surfaces for further investigations due to its energy and environmental benefits. Future work could then be carried out through CFD analysis for a five fin aluminium ICS-SWH of 1.5mm thickness. Further study assessing the structural integrity of the aluminium ICS-SWHs of 1.5 thickness should also be undertaken.

Life cycle assessment – going further

The eco-profile of an ICS-SWH would be different for any given location in the world. Scotland being a marginal weather location, somewhere with greater solar radiation potential would result in a better eco-profile of the ICS-SWH by achieving greater energy savings and therefore further reducing carbon emissions. This ICS-SWH would therefore have better applications in a sunnier climate.

The variability between LCA studies makes the comparison between studies difficult. However, it would be interesting to aggregated indices such as Tsilingiridis et al (2004) in future LCA research in order to compare with other studies.

Potential integration – going further

Health and safety issues should be addressed in order to show the actual potential of the ICS-SWH integration into dwellings and the fulfilment of the health and safety constraints towards such systems. Other issues such as planning permissions constraints could be assessed.

The integration of any SWH has a direct impact on a building including its performance and aesthetics. Integrating an ICS-SWH should not devalue the property and should contribute to achieve planning and regulatory requirements. Therefore further study on integration of such heaters in SIRS roof structure would be recommended.

The integration of the ICS-SWH into a trial house would be a good step in order to conduct seasonal performance with draw-off. Such a study of the ICS-SWH could be conducted in Scotland to assess the actual potential of the collector throughout the year.

# REFERENCES

Abdel-Rehim, Z. S. (1997) New design of solar water heater. Journal of Engineering and Applied Science, 44, 583-597.

Adelar, L., Pignolet-Tardant, F., Mara, T., Lauret, P., Garde, F. & Boyer, H. (1998) Sky temperature modelisation and applications in building simulation. Renewable Energy, 15, 418-430.

Appleyard, D. (2007) UK tidal: Ebbing it on. Renewable Energy World, 10.

Ardente, F., Beccali, G. & Cellura, M. (2003) Eco-sustainable energy and environmental strategies in design for recycling: the software ENDLESS. Ecolog Modell, 163, 101-118.

Ardente F., Beccali, G., Cellura, M. & Lo Brano, V. (2005a) Life cycle assessment of a solar thermal collector. Renewable Energy, 30, 1031-1054.

Ardente F., Beccali, G., Cellura, M. & Lo Brano, V. (2005b) Life cycle assessment of a solar thermal collector: sensitivity analysis, energy and environmental balances. Renewable Energy, 30: 109-130.

ASHRAE Standard-95 (1981) Methods of Testing to Determine the Thermal Performance of SDHW Systems. RA87, Atlanta, USA. ASHRAE.

Asif, M., Muneer, T. & Kubie, J. (2005) A value engineering analysis of timber windows. Building Service Engineering, 26, 145-155.

Asif, M. & Muneer, T. (2006) Life cycle assessment of built-in-storage solar water heaters in Pakistan. Building Service Engineering, 27, 63-69.

Asif, M., Currie, J. & Muneer, T. (2007a) Comparison of aluminium and stainless steel built-in-storage solar water heater. Building Service Engineering, 28, 337-346

Asif, M., Muneer, T. & Kelley, R. (2007b) Life cycle assessment: A case study of a dwelling home in Scotland. Building and Environment, 42, 1391-1394.

Asif, M., Currie, J. & T., M. (2007c) The role of renewable and non-renewable sources for meeting future UK energy needs. Int. J. Nuclear Governance, Economy and Ecology, 1, 372-383.

Asif, M. & Muneer, T. (2007d) Energy supply, its demand and security issues for developed and emerging economies. Renewable and Sustainable Energy Reviews, 11, 1388-1413.

BADC – British Atmospheric data Centre (2007) Online: http://badc.nerc.ac.uk/home/index.html [Accessed: 28/09/07]

Baer, S. (1975) Breadbox water heater plans. Albuquerque, New Mexico Zomeworks Corporation.

Bainbridge, D. A. (1981) Integral passive solar water heater performance. Sixth National Passive Solar Energy Conference, 163–167.

Battisti, R. & Corrado, A. (2005) Environmental assessment of solar thermal collectors with integrated water storage. Journal of Cleaner Production, 13, 1295-1300.

Berdahl, P. & Martin, M. (1984) Emissivity of clear skies. Solar Energy, 32, 663-664.

Bishop, R. C. (1983) Superinsulated batch heaters for freezing climates. Eighth National Passive Solar Conference, 807–810.

Bliss, R. W., Jr. (1959) Derivations of several ``Plate-efficiency factors`` useful in the design of flat-plate solar heat collectors. Sol. Energy; Vol/Issue: 3:4, Pages: 55-64.

BP (2007a) BP Statistical Review of World Energy 2007. Online: http://www.bp.com/statisticalreview. [Accessed on:12/03/08].

BP (2007b) Historical data - BP Statistical Review of World Energy Online: http://www.bp.com/liveassets/bp_internet/globalbp/globalbp_uk_english/reports_and_publications/statistical_energy_review_2007/STAGING/local_assets/downloads/spreadsheets/statistical_review_full_report_workbook_2007.xls. [Accessed on:12/03/08].

Brooks, F. (1936) Solar energy and its use for heating water in California, United States, Univ. Calif., Ag. Exper. Sta.

Bruce, D. M. (1994) Impact of Energy in Scotland's Environment. Society, Religion and Technology Project, Edinburgh. Church and Nation Committee.

Bucklin (2003) The Future of Today's Energy Sources. IN Hester, R. E. & Harrison, R. M. (Eds.) Sustainability and Environmental Impact of Renewable Energy Sources. The Royal Society of Chemistry - Issues in Environmental Science and Technology, 19.

Burns, S., Zeenni, E. & Guven, H. M. (1985) Stratification and performance of a solar breadbox water heater. American solar energy conference, 430–435.

Burton, J. W. & Zweig, P. R. (1981) Side by side comparison study of integral passive solar water heaters. Sixth national passive solar conference, 136–140.

Butti, K. & Perlin, J. (1980) A golden thread : 2500 years of solar architecture and technology, Palo Alto; New York, Cheshire Books ; Van Nostrand Reinhold.

Cameron, A. (2007) Marine means business: A review of the marine renewable energy sector. Renewable Energy World, 10.

Capral-Aluminium-Ltd (2006) Aluminium Information. Online: www.capral.com.au/product_info/aluminium.pdf [Accessed on:05/03/07].

Chinnappa, J. C. V. & Gnanalingam, K. (1973) Performance at Colombo, Ceylon, of a pressurised solar water heater of the combined collector and storage type. Solar Energy, 15, 195-204.

Churchill, S. W. & Chu, H. H. S. (1975) Correlating equations for laminar and turbulent free convection from a vertical plate. International Journal of Heat and Mass Transfer, 18, 1323-1329.

CIBSE (2002) TM13: Minimising the risk of Legionnaires' disease, UK, Chartered Institution of Building Services Engineers.

CIBSE Guide A. (2006) Environmental Design. London: The Chartered Institution of Building Services Engineers.

CIBSE (2007) Solar Heating Design and Installation Guide, 1st Edition, UK, Chartered Institution of Building Services Engineers.

Clarke, P., Muneer, T., Davidson, A. & Kubie, J. (2007) Models for estimation of building integrated photovoltaic systems in urban environments. IMechE, Journal of Power and Energy, 222: 61-67.

Churchill, S. W. & Chu, H. H. S. (1975) Correlating equations for laminar and turbulent free convection from a vertical plate. International Journal of Heat and Mass Transfer, 18, 1323-1329.

Communities and Local Government - CLG (2006) Code for Sustainable Homes: A step-change in sustainable home building practice, London.

Courtney, R. G. (1977) A Computer Study of Solar Water Heating. Watford. Building Research Establishment.

Crawford, R.H. & Treloar, G.J. (2004) Net energy analysis of solar and conventional domestic hot water systems in Melbourne, Australia. Solar Energy 76, 159–63.

Cristofari, C., Notton, G., Poggi, P. & Louche, A. (2003) Influence of the flow rate and the tank stratification degree on the performances of a solar flat-plate collector. International Journal of Thermal Sciences, 42, 455-469.

Cruickshank, C. A. & Harrison, S. J. (2006) Simulation and Testing of Stratified Multi-Tank, Thermal Storages for Solar Heating Systems. EuroSun 2006.

Cruz, J. M. S., Hammond, G. P. & Reis, A. J. P. S. (1999) Buoyancy-Driven Convective Heat Transfer in a Trapezoidal-Shaped Solar Collector/Thermal Store. Fifth ASME/JSME Joint Thermal Engineering Conference.

Cruz, J. M. S., Hammond, G. P. & Reis, A. J. P. S. (2002) Thermal performance of a trapezoidal-shaped solar collector/energy store. Applied Energy, 73, 195-212.

Cucumo, M., Rosa, A. D. & Marinelli, V. (2006) Experimental testing of correlations to calculate the atmospheric "transparency window" emissivity coefficient. Solar Energy, 80, 1031-1038.

Department for Environment, Food and Rural Affairs – DEFRA (2005) Guidelines for Company Reporting on Greenhouse Gas Emissions.

Department for Environment, Food and Rural Affairs - DEFRA (2007) New Bill and strategy lay foundations for tackling climate change. Online: http://www.defra.gov.uk/news/2007/070313a.htm  [Accessed: 13/03/07].

Department for Environment, Food and Rural Affairs - DEFRA (2008a) 2008 Guidelines to Defra's GHG Conversion Factors.

Department for Environment, Food and Rural Affairs - DEFRA (2008b) Climate Change Act 2008 - key provisions/milestones. Online: http://www.defra.gov.uk/environment/climatechange/uk/legislation/provisions.htm  [Accessed: 08/01/08].

Department of Trade Industry - DTI (2002) National Statistics. Energy consumption in the United Kingdoms.

Department of Trade and Industry  - DTI (2005) Estimates of hot water consumption from the 1998 EFUS. Implications for the modelling of fuel poverty in England. Online: http://www.dti.gov.uk/energy/consumers/fuel_poverty/hot_water_consumption.pdf [Accessed on:29/10/06].

Department of Trade and Industry – DTI (2007) Low Carbon Buildings Programme.

Donaldson Timber Engineering (2007) DTE’S SIRS Roofing System achieves NHBC approval. Online: http://www.amcomms.co.uk/downloads/SIRSNHBCApproval.pdf [Accessed: 14/09/08]

Duffie, J. A. & Beckman, W. A. (1974) Solar energy thermal processes, United States, John Wiley and Sons,New York, NY; University of Wisconsin-Madison, Solar Energy Laboratory, Madison, WI.

Duffie, J. A. & Beckman, W. A. (1991) Solar engineering of thermal processes, New York, John Wiley and Sons.

Ecevit, A., Al-Shariah, A. M. & Apaydin, E. D. (1989) Triangular built-in-storage solar water heater. Solar Energy, 42, 253-265.

Ecobuild 2008 Exhibition (2008) Sustainable design, construction and the built environment. Online: http://www.ecobuild.co.uk [Accessed: 25/04/08]

Energy Saving Trust (2005) Renewable energy: Factsheet 3. Online: http://www.energysavingtrust.org.uk/schri/resources/factsheets.cfm [Accessed: 28/07/08]

Energy saving trust (2007) Scottish Community Householder Renewables Initiative (SCHRI).

English-Partnership (2007) Modern Method of Construction. Online: http://www.englishpartnerships.co.uk/mmc.htm. [Accessed on:27/03/07].

English Partnership (2008) Modern Methods of Construction. Online: http://www.englishpartnerships.co.uk/mmc.htm [Accessed: 15/09/08]

Environmental-Technology-Best-Practice-Programme (2000) Life-cycle-assessment - An introduction for Industry. ET257.

Envocare.Ltd (2005) Geothermal Energy. Online: http://www.envocare.co.uk/geothermal.htm. [Accessed on:18/03/08].

ESCSTG (1989) Recommendations for performance and durability tests of solar collectors and water heating systems. Ispra, Italy. The European Solar Collector and Systems Testing Group, Commission of the European Communities, Directorate-General for Science Research and Development, Joint Research Centre.

EUROPA (2006) Domestic Hot Water – Introduction. Online: http://europa.eu.int/comm/energy_transport/atlas/htmlu/hotdintro.html [Accessed on:30/01/06].

European Insulation Manufacturers Association - ERIMA (2007) Production process: How Glass Wool is made. Online: http://www.eurima.org/ [Accessed: 08/09/08]

Fanney, A. H. & Klein, S. A. (1987) Comparison of experimental and calculated performance of integral collector-storage solar water heaters. Solar Energy, 38, 303-309.

Field, F. R., Isaacs, J. A. & Clark, J. P. (1993) Life cycle analysis and its role in product and process development. International Journal of Environmentally Conscious Design and Manufacturing, 2, 13–20.

Fuji, T. & Imura, H. (1972) Natural Convection Heat Transfer from a Plate with Arbitrary Inclination. International Journal Heat and Mass Transfer, 15, 755-767.

Furbo, S. & Mikkelsen, S. E. (1987) Is low-flow operation an advantage for solar heating systems? ISES Solar World Congress, 1, 962–966.

Fussey, D. E. & Warneford, I. P. (1978) Free convection from a downward facing inclined flat plate. International Journal of Heat and Mass Transfer, 21, 119-126.

Garg, H. P. (1975) Year round performance studies on a built-in storage type solar water heater at Jodhpur, India. Solar Energy, 17, 167-172.

Garg, H. P., Gangull, R., Puri, J. S. & Pal, R. S. (1972) Design and performance prediction of low cost solar water heater. Res Ind, 17, 125–129.

Garg, H. P. & Rani, U. (1982) Theoretical and experimental studies on collector/storage type solar water heater. Solar Energy, 29, 467-478.

Gertzos, K. P. & Caouris, Y. G. (2008) Optimal arrangement of structural and functional parts in a flat plate Integrated Collector Storage Solar Water Heater (ICSSWH). Experimental Thermal and Fluid Science, In Press, Accepted Manuscript.

Gill, A. E. (1966) The boundary-layer regime for convection in a rectangular cavity. Journal of Fluid Mechanics, 26, 515-536.

Gleick, P. H. (1994) Water and Energy. Annual Review of Energy and the Environment, Vol. 19, 267-299.

Gombert, A., Glaubitt, W., Rose, K., Dreibholz, J., Zanke, C., Blasi, B., Heinzel, A., Horbelt, W., Sporn, D., Doll, W., Wittwer, V. & Luther, J. (1998) Glazing with very high solar transmittance. Solar Energy, 62, 177-188.

Grassie, T., MacGregor, K., Muneer, T., Kubie, J. (2002) Design of a PV driven low flow solar domestic hot water system and modelling of the system collector outlet temperature. Energy Conversion and Management, 43, 1063–1078.

Grassie, T., Junaidi, H., Muneer, T., Currie, J. & Henderson, D. (2006) Study of the Modified Built-in Storage (Integrated Collector Storage) Solar Water Heater for Scottish Weather Conditions. EuroSun 2006.

Groenhout, N. K., Behnia, M. & Morrison, G. L. (2002) Experimental measurement of heat loss in an advanced solar collector. Experimental Thermal and Fluid Science, 26, 131-137.

Groover, M.P. (2006) Fundamentals of modern manufacturing: Material, Processes and Systems, 3rd Edition, New York, John Wiley and Sons.

Gull Industries (2008) ProgressivTube - Passive Solar Water Heaters. Online: http://www.gullsolar.com/index.php?page=progtube [Accessed on: 02/09/08]

Hammond, G. & Jones, C. (2006) Inventory of carbon and energy, University of Bath.

Haskell (1907) Solar Heater, USA.

Henderson, D., Junaidi, H., Muneer, T., Grassie, T. & Currie, J. (2006) Study of stratification on a integrated collector Storage Solar Water Heater. Ninth AIAA/ASME Joint Conference.

Henderson, D., Junaidi, H., Muneer, T., Grassie, T. & Currie, J. (2007) Experimental and CFD investigation of an ICSSWH at various inclinations. Renewable and Sustainable Energy Reviews, 11, 1087-1116.

Hestnes, A. G. (1999) Building Integration Of Solar Energy Systems. Solar Energy, 67, 181-187.

HMRC Treasury (2007) Budget 2007: Regulatory Impact Assessments. Governmental Report.

Hollands, K. G. T. & Lightstone, M. F. (1989) A review of low-flow, stratified-tank solar water heating systems. Solar Energy, 43, 97-105.

Hollands, K. G. T., Unny, T. E., Raithby, G. D. & Konicek, L. (1976) Free convective heat transfer across inclined air layers. AIChE--ASME national heat transfer conference, 98, 189-193.

Hottel, H. & Whillier, A. (1955) Evaluation of flat-plate solar collector performance. Trans. Conf. Use of Solar Energy, 3, 74-104.

Idso, S. B. (1981) Set of Equations for Full Spectrum and 8- to 14- mu m and 10.5- to 12.5- mu m Thermal Radiation From Cloudless Skies. Water Resources Res., 17, 295-304.

Imbabi, M. S. & Musset, A. (1996) Performance evaluation of a new hybrid solar heating and ventilation system optimised for U.K. weather conditions. Building and Environment, 31, 145-153.

Incropera, F. P. & Dewitt, D. P. Fundamentals of Heat and Mass Transfer. 5th Edition. New York, John Wiley and Sons, 2001

Institution of Engineering and Technology (IET) (2007) Solar Power. UK.

Intergovernmental Panel on Climate Change (IPCC) (2007a) Fourth Assessment Report: Climate Change 2007. Valencia, Spain. Intergovernmental Panel on Climate Change.

Intergovernmental Panel on Climate Change (IPCC) (2007b) Climate Change 2007: Impacts, Adaptation and Vulnerability. Fourth Assessment Report of the IPCC, Cambridge University Press 978 0521 88010-7.

Intergovernmental Panel on Climate Change – IPCC (2007c) Fourth Assessment Report Synthesis Report: Summary for Policymakers.

International Aluminium Institute (2007) Aluminium Properties. Online: http://www.world-aluminium.org	[Accessed on: 02/09/08]

International Atomic Energy Agency (2006) Global Uranium Resources to Meet Projected Demand. Online. [Accessed on:12/02/08].

International Energy Agency (IEA) (2006) World Energy Outlook 2006. Paris, France.

International Organization for Standardization - ISO14040 (2006) Environmental management—Life cycle assessment—Principles and framework.

International Stainless-steel Forum - ISSF (2007) 2007 Stainless steel production down after nickel-price collapse. Online: http://www.worldstainless.org/ [Accessed: 08/09/08]

ISO-14040 (2006) Environmental management -- Life cycle assessment -- Principles and framework.

Jacobson, R. Microsoft Excel 2002 Visual Basic for Applications STEP BY STEP. Redmond – USA, Microsoft Press, 2001.

Jaehnig, D., Isaksson, C., Fink, C. & Mu, T. (2007) Built for the sun: Solar thermal collectors as architectural elements. Renewable Energy World Magazine, 10.

Jordan, U. & Furbo, S. (2005) Thermal stratification in small solar domestic storage tanks caused by draw-offs. Solar Energy, 78, 291-300.

Junaidi, H. (2007) Thermal Model. Internal Report, Edinburgh. School of Engineering, Napier University.

Kaushik, S. C., Kumar, R. & Garg, H. P. (1995) Effect of baffle plate on the performance of a triangular built-in-storage solar water heater. Energy Conversion and Management, 36, 337-342.

Kaushik, S. C., Kumar, R., Garg, H. P. & Prakash, J. (1994) Transient analysis of a triangular built-in-storage solar water heater under winter conditions. Heat Recovery Systems and CHP, 14, 337-341.

Kemp (1891) Climax Solar Water Heater, USA.

Liegme, B. V. Guide to Microsoft Excel 2002 for Scientists and Engineers,3rd Edition, Elsevier, 2000.

London Metal Exchange - LME (2008) Primary Aluminium price graph. Online: http://www.lme.com/aluminium_graphs.asp [Accessed on: 02/09/08]

Luiz, A. M. (1985) Como aproveitar a energia solar, Sao Paulo, Brasil, Editora Edgard Blucher.

Management Engineering & Production Services - MEPS (2008) World Stainless steel prices. Online:  http://www.meps.co.uk/Stainless%20Prices.htm [Accessed on: 02/09/08]

MacGregor, A. W. K. & Balmbro, D. (1984) Why North is best for solar heating of building? Where are the best place in Sctoland for solar spacve heating? NorthSun 84: International Conference on Solar Energy at High Latitudes, 76.

Maplecroft net Ltd (2007a) Energy security risk. Online: http://maps.maplecroft.com/loadmap?template=min&issueID=32. [Accessed on:28/03/08].

Maplecroft net Ltd (2007b) Greenhouse gas emissions. Online: http://maps.maplecroft.com/showtext?issue=30&topic=summary. [Accessed on:28/03/08].

McCracken, H. (1978) How to build a passive solar water heater. Alturas, California, USA Carlos.

McDonald, S. (2007) Offshore transmission: Offshore options for grid connection. Renewable Energy World, 10.

McLennan, C. (2006) Solar Water Heating. Edinburgh. School of Engineering, Napier University.

Mearig, T., Coffee, N. & Morgan, M.. (1999) Life Cycle Cost Analysis Handbook, State of Alaska - Department of Education & Early Development, 1st Edition.

Met Office (2003) European summer heatwave 2003. Online: http://www.metoffice.gov.uk/education/secondary/students/european_heatwave/index.html. [Accessed.

Mirasgedis, S., Diakoulaki, D. & Assimacopoulos D. (1996) Solar energy and the abatement of atmospheric emissions. Renewable Energy, 7, 329-38.

Mohamad, A. A. (1997) Integrated solar collector-storage tank system with thermal diode. Solar Energy, 61, 211-218.

Moll, M. (2006) Stainless Steel & Special Alloys Committee meeting in Beijing - Steel & Metals Market Research. Stainless-steel Market report.

Morrison, G. L., Budihardjo, I. & Behnia, M. (2004) Water-in-glass evacuated tube solar water heaters. Solar Energy, 76, 135-140.

Munari Probst, M. C. & Roecker, C. (2007) Towards an improved architectural quality of building integrated solar thermal systems (BIST). Solar Energy, 81, 1104-1116.

Muneer, T. (1985) Effect of design parameters on performance of built-in-storage solar water heaters. Energy Conversion and Management, 25, 277-281.

Muneer, T. (2001) Solar Energy Kempe's Engineer's Yearbook. 106th ed. Tonbridge, Miller Freeman.

Muneer, T. & Hawas, M. M. (1984) Experimental study of the thermosyphonic and built-in storage type solar water heaters. Energex 84 conference, 497–500.

Muneer, T., Kubie, J. and Grassie, T. Heat Transfer – A problem solving approach. London, Taylor and Francis, 2003.

Muneer, T., Maubleu, S. & Asif, M. (2006a) Prospects of solar water heating for textile industry in Pakistan. Renewable and Sustainable Energy Reviews, 10, 1-23.

Muneer, T., Younes, S., Lambert, N. & Kubie, J. (2006b) Life cycle assessment of a medium-sized photovoltaic facility at a high latitude location. Proceedings of the Institution of Mechanical Engineers, Part A: Journal of Power and Energy, 220, 517-524.

Natural Gas Supply Association (2004) Natural Gas and the Envrionment. Online: http://www.naturalgas.org/environment/naturalgas.asp#greenhouse/. [Accessed on:12/03/08].

OECD – Organisation for Economic Co-operation and development (2008) Environmental Outlook to 2030

Offsite 2007 Exhibition – BRE zero carbon homes (2007) Modern Method of Construction and off-site systems and innovative technology. Online: www.offsite2007.com [Accessed: 10/08/07]

Ozoe, H. & Fuji, K. (1983) Long rolls generated by natural convection in an inclined, rectangular enclosure. International journal of heat and mass transfer, 26, 1427-1438.

Ozoe, H., Sayama, H. & Churchill, S. W. (1974a) Natural Convection in an Inclined Rectangular Channel at Various Aspect Ratios and Angles – Experimental Measurements. International Journal of Heat Mass Transfer, 18, 1425-1431.

Ozoe, H., Sayama, H. & Churchill, S. W. (1974b) Natural Circulation in an Inclined Rectangular Channel at Heated on one Side and Cooled on the Opposing Side. International Journal of Heat Mass Transfer, 17, 1209-1217.

Parliamentary Office of Science and Technology (2003) Modern Methods of house building, Postnote, 209.

Perers (2003) About the sky temperature, Solar Energy laboratory – The University of Wisconsin, USA. Online: http://sel.me.wisc.edu/trnsys/mailinglist/archive2003/msg00095.html [Accessed on: 07/08/08]

Pérez-Garcia, M. (2004) Simplified modelling of the nocturnal clear sky atmospheric radiation for environmental application. Ecological Modelling, 180, 395-406.

Pehnt, M. (2005) Dynamic life cycle assessment (LCA) of renewable energy technologies. Renewable Energy, 31, 55-71.

Prakash, J., Garg, H. P., Kumar, R. & Kaushik, S. C. (1992) Triangular built-in-storage solar water heater. National Energy Conference, 28–31.

REN21 (2008) Renewable Energy Policy Network for the 21st Century - Renewables 2007 Global Status Report. Online: http://www.ren21.net/pdf/RE2007_Global_Status_Report.pdf. [Accessed on:12/03/08].

Reddy, K. S. & Kaushika, N. D. (1999) Comparative study of transparent insulation materials cover systems for integrated-collector-storage solar water heaters. Solar Energy Materials and Solar Cells, 58, 431-446.

Reiss, J. & Bainbridge, D. A. (1978) Breadbox designs. Alternative Sources Energy, 46, 16–21.

Santamouris, M. & Asimakopoulos, D. Passive cooling of buildings, London, James & James, 1996.

Scottish Community and Householder Renewables Initiative - SCHRI (2008) Accredited Installer List July 2008. Online: http://www.energysavingtrust.org.uk/uploads/documents/housingbuildings/Latest%20Installer%20List4.pdf. [Accessed: 28/07/08].

Scottish Executive (Government) (2003) Securing a Renewable Future: Scotland’s renewable Energy. Astron B29409 3/03

Scottish Executive (2006) Scottish Energy Study - Volume 1 - Energy in Scotland, Supply and Demand (2006) Online: http://www.scotland.gov.uk/Publications/2006/01/19092748/0. [Accessed: 28/07/08]

Scottish Executive (2007) The Renewables Obligation (Scotland) – Order 2007.

Scottish Solar Energy Group – SSEG (2008) How much energy is saved by installing a solar water panel? Online: http://www.sseg.org.uk/index.php [Accessed: 28/07/08]

Sims, R. E. H. (2004) Renewable Energy: A response to climate change. Solar Energy, 38, 271-274.

Smyth, M., Eames, P. C. & Norton, B. (1999) A comparative performance rating for an integrated solar collector/storage vessel with inner sleeves to increase heat retention. Solar Energy, 66, 291-303.

Smyth, M.., Eames, P.C. & Norton, B. (2000) Life Cycle Assessment of a Heat Retaining Integrated Collector/Storage Solar Water Heater (ICSSWH). Energy for the 21st Century World Renewable Energy Congress VI, Brighton, 210, 1036-1040.

Smyth, M., Eames, P. C. & Norton, B. (2001) Evaluation of a freeze resistant integrated collector/storage solar water-heater for northern Europe. Applied Energy, 68, 265-274.

Smyth, M., Eames, P. C. & Norton, B. (2003) Heat retaining integrated collector/storage solar water heaters. Solar Energy, 75, 27-34.

Smyth, M., Eames, P. C. & Norton, B. (2006) Integrated collector storage solar water heaters. Renewable and Sustainable Energy Reviews, 10, 503-538.

Sokolov, M. & Vaxman, M. (1983) Analysis of an integral compact solar water heater. Solar Energy, 30, 237-246.

Soponronnarit, S., Taechapiroj, C. & Tia, S. (1994) Comparative studies of built-in-storage solar water heaters. RERIC International Energy Journal, 16, 11-26.

Stern Review: The Economics of Climate Change. (2006) Cambridge University Press

Stickney, B. L. & Nagy, C. (1980) Performance comparisons of several passive solar water heate. Fifth national passive solar conference, 1071–1075.

Stone Roofing Association (2008) Stone slate weights and roof loadings. Online:  http://www.stoneroof.org.uk/weight.html [Accessed: 14/09/08]

Šúri, M., Huld, T. A., Dunlop, E. D. & Ossenbrink, H. A. (2007) Potential of solar electricity generation in the European Union member states and candidate countries. Solar Energy, 81, 1295–1305.

Swinbank, W. C. (1963) Long-wave radiation from clear skies. Quarterly Journal of the Royal Meteorological Society, 89, 339-348.

Taborianski, V. M. & Prado, R. T. A. (2004) Comparative evaluation of the contribution of residential water heating systems to the variation of greenhouse gases stock in the atmosphere. Building and Environment, 39, 645-652.

Tan, R. B. H. & Khoo, H. H. (2005) An LCA study of a primary aluminum supply chain. Journal of Cleaner Production, 13, 607-618.

Tanishita, I. (1970) Present situation of commercial solar water heaters in Japan, United States, ISES.

Tiller, J. S. & Wochatz, V. (1982) Performance of integrated passive solar water heaters (breadbox-type) under varying design conditions in the south-eastern US. Seventh national passive solar conference, 975–980.

Tripanagnostopoulos, Y. & Souliotis, M. (2004) Integrated collector storage solar systems with asymmetric CPC reflectors. Renewable Energy, 29, 223-248.

Tripanagnostopoulos, Y. & Yianoulis, P. (1992) Integrated collector-storage systems with suppressed thermal losses. Solar Energy, 48, 31-43.

Tsilingiridis, G., Martinopoulos, G. & Kyriakis, N. (2004) Life cycle environmental impact of a thermosyphonic domestic solar hot water system in comparison with electrical and gas water heating. Renewable Energy, 29, 1277-88.

UN (1992) United Nations Framework Convention on Climate Change. United Nations.

UNEP & UNFCCC (2001) Climate Change Information Kit. France. United Nations Environment Programme - United Nations Framework Convention on Climate Change.

UNFCC (2008) Kyoto Protocol. Online: http://unfccc.int/kyoto_protocol/items/2830.php [Accessed: 25/07/08]

UK-Census (2001) Online: http://www.statistics.gov.uk/census2001/profiles/uk.asp. [Accessed on:12/12/05].

Van Berkel, J. (1996) Mixing in thermally stratified energy stores. Solar Energy, 58, 203-211.

Van Koppen, C. W. J., Thomas, J. P. S. & Veltkamp, W. B. (1979) The actual benefits of thermally stratified storage in a small and medium size solar system. ISES Biennial Meeting, 2, 576–580.

Van Niekerk, W. M. K., du Toit, C. G. & Scheffler, T. B. (1996) Performance modelling of a parallel tube polymer absorber. Solar Energy, 58, 39-44.

Velazquez, N. (2006) Impact of Rising Energy Costs on Small Business. Congress of the United States, House of Representatives.

VELUX (2005) VELUX Flashings 4 - Brochure

Weir, G. & Muneer, T. (1998) Energy and environmental impact analysis of double-glazed windows. Energy Conversion and Management, 39, 243-256.

Whittle, G. E. (1978) The Efficiency of Domestic Hot Water Production Out of the Heating Season. Watford. Building Research Establishment.

World Energy Council (2004) 2004 SURVEY OF ENERGY RESOURCES, Elsevier.

World Energy Council (2007) 2007 SURVEY OF ENERGY RESOURCES, Elsevier.

World Health Organisation (2008) 10 facts on climate change and health. Online: http://www.who.int/features/factfiles/climate_change/en/index.html [Accessed: 22/07/08]

Wood, J. (2008) Modern Methods of Construction: Structural Insulated Roof System. Internal Report. Napier University.

Yang, Y. (2003) Natural convective flow and heat transfer in vertical and inclined glazing cavities. Mechanical and Industrial Engineering,University of Massachusetts Amherst. Master of Science.

Zhong, Z. Y., Yang, K. T. & Lloyd, J. R. (1985) Variable-property Natural convection in tilted Enclosures with Thermal Radiation. Numerical Methods in Heat Transfer, 3.

# APPENDICES

APPENDIX A: GLOSSARY OF TERMS

APPENDIX B: LIST OF PUBLICATIONS

APPENDIX C: THERMAL MODELS

APPENDIX A

GLOSSARY OF TERMS

Energy mix: The combination of sources used to provide energy at any given time and place.

Traditional biomass:  It represents unprocessed biomass including forest product waste, collected fuel wood, agricultural waste and animal dung that are burned in stoves or furnaces to provide heat energy for cooking, heating and agricultural and industrial processing, typically in rural areas.

Degree-days: The rate of heat loss from a building, (related to the building fabric) and the temperature difference between the inside and outside of a building - the greater the temperature difference the more heat will be lost.

Atmospheric transparency window: The atmosphere behaves like a black body throughout the infrared spectrum with the exception of the wavelength interval between 8 -14(m. The so-called Atmospheric Transparency Window is located between these two extremes and is characterised by a high transparency to infrared thermal radiation and therefore by low energy emission.

Environment:  The term environment represents the external conditions including temperature, wind speed, irradiation, cloud cover etc with which the SWH interacts.

Clear sky index: Corresponding to the ratio of the global horizontal irradiance to the global horizontal irradiance under clear sky conditions.

Solar fraction: The solar fraction is the amount of energy provided by the solar technology divided by the total energy required.

APPENDIX B

LIST OF PUBLICATIONS

Currie, J.I., Garnier, C., Muneer, T., Henderson, D., Grassie, T. (2007) Comparison of Finned Aluminium and Steel Integrated Collector Storage Solar Water Heater, SOLARIS 2007, 3rd International Conference on Solar Radiation and Day Lighting, New Delhi.

Currie, J.I., Garnier, C., Muneer, T., Grassie, T., Henderson, D. (2008) Modelling bulk water temperature in integrated collector storage systems. Building Services Engineering Research and Technology (Published)

Garnier, C., Currie, J.I., Muneer, T. and Girard, A. (2008) Computational study of an integrated collector storage solar water heater, EUROSUN 2008, International Conference on Solar Heating, Cooling and Buildings, Lisbon.

Garnier, C., Currie, J.I. and Muneer, T. (2008) Integrated collector storage solar water heater: Temperature stratification. Applied Energy (Accepted for publication)

Garnier, C., Currie, J.I. and Muneer, T. (2008) Integrated collector storage solar water heater: Life Cycle Assessment. Journal of Cleaner Production (Communicated for publication)

Garnier, C., Muneer, T. and Currie, J.I. (2008) Mathematical modelling of integrated collector storage systems under real weather conditions. American Society of Mechanical Engineers (Communicated for publication)

APPENDIX C

SOLAR THERMAL ENERGY SYSTEM FOR HOUSING (STESH)

FIELD THERMAL MODELS

STESH – Field model program

Fig. C1: Caption of STESH programme welcome page

Sub compute01()

Collsize = Sheets("Site-System Input").Range("G22").Value

Depth = Sheets("Site-System Input").Range("G23").Value

Thickness = Sheets("Site-System Input").Range("G24").Value

Longueur = Sheets("Site-System Input").Range("G25").Value

Volume = Collsize * Depth

Ac = Longueur * Thickness

Peri = 2 * (Thickness + Longueur)

finarea = 0

' Depends on choice

If Sheets("Site-System Input").Range("G27").Value = "No" Then finarea = 0

If Sheets("Site-System Input").Range("G27").Value = "Yes" Then finarea = 4 * 0.002 * Longueur

InTw = Sheets("Site-System Input").Cells(19, 7).Value + 273.15

Sheets("Site-System Input").Cells(20, 7).Value = InTw

Tw = Sheets("Meteorological Input").Cells(8, 21).Value 'Site-System Input water temp.

For x = 8 To 127

Tam = Sheets("Meteorological Input").Cells(x, 6).Value

Vel = Sheets("Meteorological Input").Cells(x, 7).Value

CloudCover = Sheets("Meteorological Input").Cells(x, 8).Value

RefMidnight = Sheets("Meteorological Input").Cells(x, 3).Value

Ep = 0.95

Aw = 1 'm2

Angle = Sheets("Site-System Input").Range("H14").Value

Gin = 0.8 * Sheets("Meteorological Input").Cells(x, 20).Value

mcp = Sheets("Site-System Input").Cells(29, 7).Value

kmaterial = Sheets("Site-System Input").Cells(30, 7).Value

mcwater = 208.323 'kJ/K

mcinsul = 2.897 'kJ/K

mcwood = 37.32 'kJ/K

mcglazing = 10.56 'kJ/K

mcin = 3.37637 'kJ/K

Ta = Tam + 273.15

'Tsky = Ta

hwind = 8.55 + 2.56 * Vel

Eg = 0.88

' Initialisation of Tp & Tc

Tp = Tw + 0.5

Tc = Tp - ((Tp - Ta) / 3)

deltime = 360

For iminute = 1 To 10

'Start iterative loop

For i = 1 To 10

Tdpclear = (0.7105 * (Ta - 273.15) - 0.7864)

Tdpovercast = (0.8231 * (Ta - 273.15) - 0.8119)

If 0 <= CloudCover < 3 Then

Tdp = Tdpclear

EmisS = 0.747 + 0.594 * (Tdp / 100) - 0.551 * ((Tdp / 100) ^ 2)

If 3 <= CloudCover <= 5 Then

Tdp = (Tdpclear + Tdpovercast) / 2

EmisS = (0.747 + 0.594 * (Tdp / 100) - 0.551 * ((Tdp / 100) ^ 2)) * (1 + 0.0224 * 0.5 - 0.0035 * (0.5 ^ 2) + 0.00028 * (0.5 ^ 3))

If 5 < CloudCover Then

Tdp = Tdpovercast

EmisS = (0.747 + 0.594 * (Tdp / 100) - 0.551 * ((Tdp / 100) ^ 2)) * (1 + 0.0224 - 0.0035 + 0.00028)

End If

End If

End If

Esky = 1 + ((107952 * (1 - EmisS)) / ((Ta ^ 2) - 680.8 * Ta + 73594.9)

Fsky = 1 / ((1 / Eg) + (1 / Esky) - 1)

CoordoA = 15 * RefMidnight

CoordoB = 0.711 + 0.0056 * Tdp + 0.000073 * Tdp ^ 2

CoordoC = Cos((CoordoA) ^ (1 / 4))

Tsky = Ta * (CoordoB + 0.013 * CoordoC)

Ucar = (Fsky * 0.0000000567 * (Tc ^ 4 - Tsky ^ 4)) / (Tc - Tsky)

Ucac = hwind

Uca = Ucac + Ucar

BEmm = (1 / Eg) + (1 / Ep) - 1

Upcr = (0.0000000567 * (Tp + Tc) * (Tp ^ 2 + Tc ^ 2)) / BEmm

'Calculation of Rayliegh number for air cavity

Tfag = (Tp + Tc) / 2

Sheets("AirProp").Range("J13").Value = Tfag

visair = Sheets("AirProp").Range("Q18").Value

kfag = Sheets("AirProp").Range("R18").Value

visair = visair * 0.000001

Raag = (9.81 * (1 / Tfag) * (Tp - Tc) * 1 ^ 3) / (visair)

'Calculation of Nu for air cavity by Holland Regression

term1 = 1.44 * (1 - (1708 / Raag * Cos(Angle)))

term2 = 1 - ((1708 * Sin(1.8 * Angle) ^ 1.6) / (Raag * Cos(Angle)))

term3 = ((Raag * Cos(Angle) / 5830) ^ (1 / 3)) - 1

term4 = Application.Max(term1, 0)

term5 = Application.Max(0, term3)

Nuag = 1 + term2 * term4 + term5

'calculation of total conductance form plate to glass cover

Upcc = Nuag * kfag * 0.001 / (0.025)

Upc = Upcc + Upcr

'Calculation of Rayleigh Number for Water

Sheets("WaterProp").Range("Q24").Value = 0.5 * (Tw + Tp)

Speheatw = Sheets("WaterProp").Range("AA29").Value

Betaw = Sheets("WaterProp").Range("AJ29").Value

Prw = Sheets("WaterProp").Range("AK29").Value

Visw = 0.000001 * Sheets("WaterProp").Range("AC29").Value

denw = Sheets("WaterProp").Range("W29").Value

kw = 0.001 * Sheets("WaterProp").Range("AE29").Value

Raw = Prw * 9.81 * Betaw * 0.000001 * (1 ^ 3) * (Tp - Tw) / ((Visw / denw) ^ 2)

If (Raw <= 0) Then Raw = Sqr((Raw) ^ 2)

'Calcuating water conductance

Nuw = 0.56 * ((Raw * Cos(Angle)) ^ 0.25) * ((1 / 0.05) ^ (1 / 6))

hw = Nuw * kw / 1

Uw = hw

'Back losses

UAbloss = 0.35

' Iterations for Tp & Tc

Tp = (Gin + Upc * Tc + Uw * Tw) / (Upc + Uw)

Tc = (Upc * Tp + Ucac * Ta + Ucar * Tsky) / (Upc + Ucac + Ucar)

Next i

Qpw = Uw * (Tp - Tw)

Qpc = Upc * (Tp - Tc)

'Fin lengh calculation and improvement factor

smallm = 335 * 2 * (Longueur + Thickness) / (kmaterial * Longueur * Thickness)

smallm = Sqr(smallm)

ml = smallm * Depth

BigM = Sqr(335 * Peri * kmaterial * Ac * (Tp - Tw))

'Af = 2 * (Depth * Thickness) + 2 * (Depth * Longueur) + (Longueur * Thickness)

For j = 7 To 32

Length = Sheets("Fin Effect").Cells(j, 1).Value

tetab = Application.Cosh(ml)

teta = Application.Cosh(smallm * (Depth - (Length * 0.001)))

tetax = (teta / tetab) * Abs(Tp - Tw)

Tfin = tetax + Tw

Rafin = Prw * 9.81 * Betaw * 0.000001 * ((Depth / Cos(Angle)) ^ 3) * (Tfin - Tw) / ((Visw / denw) ^ 2)

Nufin = 0.68 + (0.67 * Rafin ^ 0.28) / (1 + (0.492 / Prw) ^ (9 / 16)) ^ (4 / 9)

hfin = Nufin * kw / (Depth / Cos(Angle))

Qxfin = hfin * (Tfin - Tw) * finarea

Sheets("Fin Effect").Cells(j, 2).Value = tetax

Sheets("Fin Effect").Cells(j, 3).Value = Tfin - 273.15

Sheets("Fin Effect").Cells(j, 4).Value = hfin

Sheets("Fin Effect").Cells(j, 5).Value = Qxfin

tetao = Sheets("Fin Effect").Cells(7, 3).Value - Sheets("Fin Effect").Cells(32, 3).Value

limittetao = 0.1 * tetao

Sheets("Fin Effect").Cells(7, 6).Value = tetao

Sheets("Fin Effect").Cells(7, 7).Value = limittetao

'Fin Effeciency

Lc = (Length * 0.001)

mLc = smallm * Lc

Ap = Lc * Thickness

Fineffi = Application.Tanh(mLc) / (mLc)

Sheets("Fin Effect").Cells(j, 15).Value = Fineffi

Next j

Dim D(25)

Dim E(25)

D(0) = Sheets("Fin Effect").Cells(7, 1).Value

D(1) = Sheets("Fin Effect").Cells(8, 1).Value

D(2) = Sheets("Fin Effect").Cells(9, 1).Value

D(3) = Sheets("Fin Effect").Cells(10, 1).Value

D(4) = Sheets("Fin Effect").Cells(11, 1).Value

D(5) = Sheets("Fin Effect").Cells(12, 1).Value

D(6) = Sheets("Fin Effect").Cells(13, 1).Value

D(7) = Sheets("Fin Effect").Cells(14, 1).Value

D(8) = Sheets("Fin Effect").Cells(15, 1).Value

D(9) = Sheets("Fin Effect").Cells(16, 1).Value

D(10) = Sheets("Fin Effect").Cells(17, 1).Value

D(11) = Sheets("Fin Effect").Cells(18, 1).Value

D(12) = Sheets("Fin Effect").Cells(19, 1).Value

D(13) = Sheets("Fin Effect").Cells(20, 1).Value

D(14) = Sheets("Fin Effect").Cells(21, 1).Value

D(15) = Sheets("Fin Effect").Cells(22, 1).Value

D(16) = Sheets("Fin Effect").Cells(23, 1).Value

D(17) = Sheets("Fin Effect").Cells(24, 1).Value

D(18) = Sheets("Fin Effect").Cells(25, 1).Value

D(19) = Sheets("Fin Effect").Cells(26, 1).Value

D(20) = Sheets("Fin Effect").Cells(27, 1).Value

D(21) = Sheets("Fin Effect").Cells(28, 1).Value

D(22) = Sheets("Fin Effect").Cells(29, 1).Value

D(23) = Sheets("Fin Effect").Cells(30, 1).Value

D(24) = Sheets("Fin Effect").Cells(31, 1).Value

D(25) = Sheets("Fin Effect").Cells(32, 1).Value

E(0) = Sheets("Fin Effect").Cells(7, 5).Value

E(1) = Sheets("Fin Effect").Cells(8, 5).Value

E(2) = Sheets("Fin Effect").Cells(9, 5).Value

E(3) = Sheets("Fin Effect").Cells(10, 5).Value

E(4) = Sheets("Fin Effect").Cells(11, 5).Value

E(5) = Sheets("Fin Effect").Cells(12, 5).Value

E(6) = Sheets("Fin Effect").Cells(13, 5).Value

E(7) = Sheets("Fin Effect").Cells(14, 5).Value

E(8) = Sheets("Fin Effect").Cells(15, 5).Value

E(9) = Sheets("Fin Effect").Cells(16, 5).Value

E(10) = Sheets("Fin Effect").Cells(17, 5).Value

E(11) = Sheets("Fin Effect").Cells(18, 5).Value

E(12) = Sheets("Fin Effect").Cells(19, 5).Value

E(13) = Sheets("Fin Effect").Cells(20, 5).Value

E(14) = Sheets("Fin Effect").Cells(21, 5).Value

E(15) = Sheets("Fin Effect").Cells(22, 5).Value

E(16) = Sheets("Fin Effect").Cells(23, 5).Value

E(17) = Sheets("Fin Effect").Cells(24, 5).Value

E(18) = Sheets("Fin Effect").Cells(25, 5).Value

E(19) = Sheets("Fin Effect").Cells(26, 5).Value

E(20) = Sheets("Fin Effect").Cells(27, 5).Value

E(21) = Sheets("Fin Effect").Cells(28, 5).Value

E(22) = Sheets("Fin Effect").Cells(29, 5).Value

E(23) = Sheets("Fin Effect").Cells(30, 5).Value

E(24) = Sheets("Fin Effect").Cells(31, 5).Value

E(25) = Sheets("Fin Effect").Cells(32, 5).Value

limdist = Sheets("Fin Effect").Cells(7, 8).Value

Total = E(0)

distance = D(0)

Cnt = 0

Do While (distance < limdist)

Cnt = Cnt + 1

distance = D(Cnt)

Total = Total + E(Cnt)

Loop

Total = Total - E(Cnt)

Qfin = Total

Improvfactor = 1 + (Qfin / Qpw)

FinT = Sheets("Fin Effect").Cells(34, 3).Value

Quseful = 0.001 * deltime * (Uw * Aw * (Tp - Tw) + Qfin - UAbloss * (Tw - Ta))

Tw = Tw + Quseful / (mcwater + mcp + mcinsul + mcwood + mcglazing + mcin)

Next iminute

Sheets("Meteorological Input").Cells(x, 22).Value = Uca

Sheets("Meteorological Input").Cells(x, 23).Value = Upc

Sheets("Meteorological Input").Cells(x, 24).Value = Uw

Sheets("Meteorological Input").Cells(x, 25).Value = Tp

Sheets("Meteorological Input").Cells(x, 26).Value = Tc

Sheets("Meteorological Input").Cells(x, 27).Value = Qpw

Sheets("Meteorological Input").Cells(x, 28).Value = Qpc

Sheets("Meteorological Input").Cells(x, 29).Value = Qfin

Sheets("Meteorological Input").Cells(x, 30).Value = Quseful

Sheets("Meteorological Input").Cells(x, 31).Value = Improvfactor

Sheets("Meteorological Input").Cells(x + 1, 21).Value = Tw

Next x

End Sub

# Text boxes

Simulated

“Roof structure”

Cold water tank

2

1

Stainless-steel collector

bottom end

Aluminium collector

top end

Aluminium collector

bottom end

b

a

Variac

Voltmeter

Ammeter

Wattmeter

Load / Electrically heated silicone rubber pad

b

a

b

a

Silicone

Silicone nodes

Electrically heated silicone rubber pad

Thermocouple tip

Data Logger

Type K-single Thermocouples

Reference Thermometer

SP

FR

DN

SW

UK

AU

CY

MA

GR

Constant temperature bath

0 – 1.5

1.5 – 3.0

3.0 – 4.5

4.5 – 5.0

>0.5

Hot water

Data Loggers

Type K-single Thermocouples

Reference Thermometer

Thermos flask

Ice

Computer Installation

Top Cover

Air cavity

Water cavity

Heat losses

Heat gains

Tw

Air cavity

Water cavity

Ta

Qlosses

Tc

Tp

QUseful

Glass cover

Insulation

Absorber plate

Tp

Input Heat Flux or Solar radiation, G((()

Calculation of Tw from QUseful

Update time step, t: i = i + 1

i = 10*

END

Check

i

Update Tp and Tc

i = i + 1

Calculation of Uca and Upc

Inlet water temperature, Tw

Initialisation of Tp and Tc

Ambient temperature, Ta

Cloud cover, CC

Calculation of Tdp

Calculation of TSky and (Sky

Air properties at film temperature, Tfa

Wind velocity Vw

Cover and plate emissivity, (c, (p

Water properties at film temperature Tfw

Calculation of   QFins

Calculation of QUseful

Calculation of   Tp and Tc

(eq. 4.24 – 4.25)

Calculation of    Upw

Calculation of    Uwa

Check

i = 10

i = 10

i < 10

i < 10*

20hrs

10hrs

15hrs

5hrs

1 hr

Higher velocities

Higher velocities

Glass Cover

Glass wool insulation

Collector

Wooden box

a

b

1

2

3

4

5

6

GER

Cool surface

Hot surface

Glass cover

Air cavity

Glass wool insulation

Heated surface / Absorber plate

Fins

Wooden container

Water tank

1235 mm

180 mm

Stainless-steel collector

top end